## Sheet1
0 | 1 | AT1 | AT2 | AT3 | AT4 | AT5 | AT6 | AT7 | AT8 | AT9 | AT10 | LT1 | LT2 | LT3 | LT4 | LT5 | LT6 | P1 | P2 | RH1 | RH2 | RH3 | RH4 | RH5 | RH6 | RH7 | RH8 | W1 | W2 | W3 | W4 | W5 | W6 | W7 | W8 | kWh | Watt | valid_times | TimeDifference | Total_Power | U_Config | Super_Heat | Sub_Cool | T_supply | T_return | dT[C] | W_U_Inlet | W_S_Inlet | W_exhaust | RH_avg | W_supply | Exhaust Humidity Delta (Standard) | Exhaust Humidity Delta (Averaged Inlet) | Supply Humidity Delta (Standard) [g/kg] | Supply Humidity Delta (Averaged Inlet) | Process_airflow | Process V_dot | Process M_dot [kg/s] | Regen Airflow | Regen V_dot | Regen M_dot [kg/s] | Q_lat_Supply [W] | Q_lat_Supply Filtered[W] | Q_lat_Supply [BTU/hr] | Q_lat_Supply Filtered[BTU/hr] | Q_sens [W] | Q_sens [BTU/hr] | Q_lat_Exhaust [W] | Q_lat_Exhaust Filtered[W] | Q_lat_Exhaust [BTU/hr] | Q_lat_Exhaust Filtered[BTU/hr] | Q_tot (Exhaust Latent) [BTU/hr] | Q_tot (Supply Latent) [BTU/hr] | EER (Exhaust Latent) [BTU/Wh] | EER (Supply Latent) [BTU/Wh] | Average_Power_5min | Average_Q_tot_5min | EER_5min | Q_lat_5min
| 17:11:14 | 24.65 | 34.41 | 23.8 | 19.18 | 17.97 | 17.72 | 17.3 | 17.16 | 19.13 | 19.58 | 18.52 | 13.41 | 11.98 | 64.27 | 40.72 | 39.32 | 148.56 | 359.74 | 54.99 | 53.1 | 32.57 | 74.82 | 79.62 | 66.85 | 0 | 0 | 10.33 | 11.14 | 10.16 | 9.71 | -1 | -1 | -1 | -1 | 381.02 | 744 | 17:11:14 | 0 | 744 | 0 | 0 | 0 | 18.0767 | 24.65 | 6.5733 | 10.1174 | 10.2832 | 11.0831 | 77.22 | 9.9897 | 0 | 0 | 0.32461 | 0.40985 | 615 | 0.29025 | 0.34249 | 395 | 0.18642 | 0.21997 | 251.2593 | 317.236 | 856.7943 | 1081.7746 | 2264.8237 | 7723.0488 | 0 | 0 | 0 | 0 | 7723.0488 | 8804.8234 | 10.3804 | 11.8344 | 728 | 8174.563 | 11.2354 | 700.2026
| 17:11:25 | 24.68 | 34.47 | 23.94 | 18.99 | 18.11 | 17.7 | 17.35 | 17.17 | 19.12 | 19.53 | 18.61 | 13.46 | 12 | 64.41 | 40.77 | 39.42 | 148.92 | 360.24 | 54.79 | 52.89 | 32.02 | 75.11 | 79.61 | 67.13 | 0 | 0 | 10.31 | 10.98 | 10.21 | 9.73 | -1 | -1 | -1 | -1 | 381.02 | 746 | 17:11:25 | 0.18333 | 746 | 0 | 0 | 0 | 18.0733 | 24.68 | 6.6067 | 10.1666 | 10.2606 | 10.9297 | 77.36 | 10.0059 | 0 | 0 | 0.28568 | 0.39358 | 615 | 0.29025 | 0.34249 | 395 | 0.18642 | 0.21997 | 221.1292 | 304.6412 | 754.0507 | 1038.8264 | 2276.3086 | 7762.2123 | 0 | 0 | 0 | 0 | 7762.2123 | 8801.0387 | 10.4051 | 11.7976 | 730.8 | 8044.0497 | 11.0173 | 423.2178
| 17:11:37 | 24.57 | 34.58 | 23.86 | 19.01 | 18.03 | 17.66 | 17.29 | 17.17 | 19.27 | 19.52 | 18.57 | 13.29 | 11.93 | 64.57 | 40.81 | 39.36 | 148.1 | 360.45 | 54.57 | 52.68 | 31.8 | 75.01 | 79.81 | 67.43 | 0 | 0 | 10.2 | 10.97 | 10.12 | 9.74 | -1 | -1 | -1 | -1 | 381.02 | 746 | 17:11:37 | 0.38333 | 746 | 0 | 0 | 0 | 18.0717 | 24.57 | 6.4983 | 10.0757 | 10.1511 | 10.9209 | 77.41 | 10.0114 | 0 | 0 | 0.17069 | 0.38807 | 615 | 0.29025 | 0.34249 | 395 | 0.18642 | 0.21997 | 132.1218 | 300.38 | 450.5354 | 1024.2958 | 2238.9826 | 7634.9308 | 0 | 0 | 0 | 0 | 7634.9308 | 8659.2266 | 10.2345 | 11.6075 | 736.4 | 7898.1118 | 10.7343 | 225.1923
| 17:11:47 | 24.56 | 34.69 | 23.84 | 18.84 | 17.94 | 17.71 | 17.24 | 17.04 | 19.11 | 19.44 | 18.47 | 13.3 | 11.87 | 64.67 | 40.9 | 39.43 | 148.47 | 361.19 | 53.96 | 52.25 | 30.91 | 74.99 | 79.6 | 67.71 | 0 | 0 | 10.11 | 10.73 | 9.99 | 9.69 | -1 | -1 | -1 | -1 | 381.02 | 747 | 17:11:47 | 0.55 | 747 | 0 | 0 | 0 | 17.98 | 24.56 | 6.58 | 9.9491 | 10.0608 | 10.6761 | 77.295 | 9.9379 | 0 | 0 | 0.15388 | 0.46157 | 615 | 0.29025 | 0.34249 | 395 | 0.18642 | 0.21997 | 119.1061 | 357.2719 | 406.1517 | 1218.2973 | 2267.1207 | 7730.8815 | 0 | 0 | 0 | 0 | 7730.8815 | 8949.1788 | 10.3492 | 11.9802 | 742 | 7699.5506 | 10.3775 | 0
| 17:11:57 | 24.62 | 34.73 | 23.81 | 18.88 | 17.89 | 17.66 | 17.18 | 17 | 19.03 | 19.31 | 18.36 | 13.27 | 11.87 | 64.75 | 40.96 | 39.64 | 148.26 | 361.17 | 53.76 | 52.05 | 30.7 | 75.07 | 79.57 | 67.59 | 0 | 0 | 10.1 | 10.68 | 9.94 | 9.65 | -1 | -1 | -1 | -1 | 381.02 | 746 | 17:11:57 | 0.71667 | 746 | 0 | 0 | 0 | 17.94 | 24.62 | 6.68 | 9.8935 | 10.0583 | 10.6262 | 77.32 | 9.9158 | 0 | 0 | 0.17348 | 0.4837 | 615 | 0.29025 | 0.34249 | 395 | 0.18642 | 0.21997 | 134.2775 | 374.398 | 457.8861 | 1276.6973 | 2301.5754 | 7848.3721 | 0 | 0 | 0 | 0 | 7848.3721 | 9125.0694 | 10.5206 | 12.232 | 745.8 | 7739.8891 | 10.378 | 0
| 17:12:07 | 24.69 | 34.82 | 23.89 | 18.81 | 17.9 | 17.67 | 17.2 | 16.97 | 18.92 | 19.3 | 18.19 | 13.29 | 11.92 | 64.88 | 41.08 | 39.61 | 148.44 | 362.53 | 53.96 | 52.37 | 30.48 | 75.57 | 79.88 | 68.09 | 0 | 0 | 10.21 | 10.65 | 10.02 | 9.7 | -1 | -1 | -1 | -1 | 381.02 | 748 | 17:12:07 | 0.88333 | 748 | 0 | 0 | 0 | 17.9117 | 24.69 | 6.7783 | 9.9796 | 10.1642 | 10.6024 | 77.725 | 9.9505 | 0 | 0 | 0.24473 | 0.44897 | 615 | 0.29025 | 0.34249 | 395 | 0.18642 | 0.21997 | 189.4265 | 347.5208 | 645.9443 | 1185.046 | 2335.4559 | 7963.9045 | 0 | 0 | 0 | 0 | 7963.9045 | 9148.9505 | 10.6469 | 12.2312 | 746.6 | 7788.0602 | 10.4313 | 0
| 17:12:18 | 24.45 | 34.85 | 23.68 | 18.86 | 17.91 | 17.67 | 17.22 | 16.92 | 18.93 | 19.25 | 17.9 | 13.39 | 11.98 | 64.99 | 41.14 | 39.75 | 149.21 | 362.52 | 53.96 | 52.48 | 30.27 | 75.76 | 80.18 | 68.36 | 0 | 0 | 10.09 | 10.6 | 9.89 | 9.73 | -1 | -1 | -1 | -1 | 381.03 | 729 | 17:12:18 | 1.0667 | 729 | 0 | 0 | 0 | 17.9183 | 24.45 | 6.5317 | 9.8523 | 10.0384 | 10.5459 | 77.97 | 9.9867 | 0 | 0 | 0.082788 | 0.41285 | 615 | 0.29025 | 0.34249 | 395 | 0.18642 | 0.21997 | 64.0804 | 319.5577 | 218.5141 | 1089.6918 | 2250.4676 | 7674.0943 | 0 | 0 | 0 | 0 | 7674.0943 | 8763.7861 | 10.5269 | 12.0217 | 743.2 | 7770.4366 | 10.4556 | 0
| 17:12:28 | 24.81 | 34.96 | 23.92 | 18.81 | 17.93 | 17.72 | 17.24 | 16.99 | 18.93 | 19.26 | 17.82 | 13.33 | 11.99 | 65.13 | 41.23 | 39.87 | 148.92 | 364.25 | 53.76 | 52.28 | 30.05 | 75.96 | 80.18 | 68.77 | 0 | 0 | 10.26 | 10.58 | 10 | 9.77 | -1 | -1 | -1 | -1 | 381.03 | 730 | 17:12:28 | 1.2333 | 730 | 0 | 0 | 0 | 17.9367 | 24.81 | 6.8733 | 9.9602 | 10.2207 | 10.533 | 78.07 | 10.0114 | 0 | 0 | 0.24029 | 0.3881 | 615 | 0.29025 | 0.34249 | 395 | 0.18642 | 0.21997 | 185.9884 | 300.4029 | 634.2205 | 1024.374 | 2368.1878 | 8075.5206 | 0 | 0 | 0 | 0 | 8075.5206 | 9099.8946 | 11.0624 | 12.4656 | 740 | 7858.5546 | 10.6212 | 0
| 17:12:38 | 24.68 | 34.95 | 23.56 | 18.75 | 17.9 | 17.68 | 17.19 | 16.92 | 18.9 | 19.17 | 17.62 | 13.42 | 12.01 | 65.18 | 41.28 | 39.99 | 148.37 | 364.35 | 54.38 | 52.89 | 29.94 | 76.15 | 80.49 | 69.06 | 0 | 0 | 10.31 | 10.54 | 9.9 | 9.77 | -1 | -1 | -1 | -1 | 381.03 | 732 | 17:12:38 | 1.4 | 732 | 0 | 0 | 0 | 17.89 | 24.68 | 6.79 | 9.8575 | 10.2606 | 10.4879 | 78.32 | 10.014 | 0 | 0 | 0.27757 | 0.38546 | 615 | 0.29025 | 0.34249 | 395 | 0.18642 | 0.21997 | 214.8492 | 298.3611 | 732.6357 | 1017.4114 | 2339.4756 | 7977.6117 | 0 | 0 | 0 | 0 | 7977.6117 | 8995.0231 | 10.8984 | 12.2883 | 737 | 7907.9006 | 10.731 | 0
| 17:12:49 | 24.88 | 35.01 | 23.65 | 18.81 | 17.95 | 17.75 | 17.26 | 16.96 | 18.9 | 19.17 | 17.65 | 13.45 | 12.06 | 65.23 | 41.33 | 40.04 | 149.34 | 364.71 | 54.07 | 52.37 | 29.61 | 76.34 | 80.59 | 69.25 | 0 | 0 | 10.33 | 10.45 | 9.9 | 9.82 | -1 | -1 | -1 | -1 | 381.04 | 740 | 17:12:49 | 1.5833 | 740 | 0 | 0 | 0 | 17.9383 | 24.88 | 6.9417 | 9.8546 | 10.2821 | 10.4054 | 78.465 | 10.0639 | 0 | 0 | 0.2492 | 0.33556 | 615 | 0.29025 | 0.34249 | 395 | 0.18642 | 0.21997 | 192.8874 | 259.7309 | 657.746 | 885.6824 | 2391.7319 | 8155.8058 | 0 | 0 | 0 | 0 | 8155.8058 | 9041.4882 | 11.0214 | 12.2182 | 735.8 | 7969.3874 | 10.8312 | 0
| 17:12:59 | 24.66 | 35.15 | 23.77 | 18.74 | 17.94 | 17.71 | 17.28 | 16.98 | 18.88 | 19.12 | 17.53 | 13.29 | 12.02 | 65.36 | 41.45 | 40.12 | 149.15 | 366.62 | 54.38 | 52.47 | 29.61 | 76.56 | 80.59 | 69.56 | 0 | 0 | 10.21 | 10.54 | 10.03 | 9.83 | -1 | -1 | -1 | -1 | 381.04 | 756 | 17:12:59 | 1.75 | 756 | 0 | 0 | 0 | 17.9217 | 24.66 | 6.7383 | 9.985 | 10.1654 | 10.4876 | 78.575 | 10.0675 | 0 | 0 | 0.1289 | 0.33196 | 615 | 0.29025 | 0.34249 | 395 | 0.18642 | 0.21997 | 99.7692 | 256.9455 | 340.2128 | 876.184 | 2321.674 | 7916.9083 | 0 | 0 | 0 | 0 | 7916.9083 | 8793.0922 | 10.4721 | 11.6311 | 737.4 | 7959.9881 | 10.7962 | 0
| 17:13:09 | 24.79 | 35.17 | 23.88 | 18.79 | 17.97 | 17.74 | 17.25 | 16.96 | 18.89 | 19.13 | 17.52 | 13.47 | 12.04 | 65.45 | 41.54 | 40.15 | 149.25 | 367.32 | 54.38 | 52.69 | 29.4 | 76.46 | 80.59 | 69.75 | 0 | 0 | 10.34 | 10.48 | 10.1 | 9.84 | -1 | -1 | -1 | -1 | 381.04 | 758 | 17:13:09 | 1.9167 | 758 | 0 | 0 | 0 | 17.9333 | 24.79 | 6.8567 | 10.0524 | 10.2896 | 10.4237 | 78.525 | 10.0685 | 0 | 0 | 0.25212 | 0.33096 | 615 | 0.29025 | 0.34249 | 395 | 0.18642 | 0.21997 | 195.1521 | 256.1706 | 665.4686 | 873.5417 | 2362.4454 | 8055.9388 | 0 | 0 | 0 | 0 | 8055.9388 | 8929.4805 | 10.6279 | 11.7803 | 743.2 | 8036.357 | 10.8164 | 0
| 17:13:20 | 24.74 | 35.42 | 23.69 | 18.74 | 17.98 | 17.73 | 17.24 | 16.95 | 18.89 | 19.06 | 17.59 | 13.35 | 12.08 | 65.54 | 41.72 | 40.36 | 148.79 | 368.96 | 54.17 | 52.69 | 29.18 | 76.56 | 80.58 | 69.74 | 0 | 0 | 10.31 | 10.54 | 9.94 | 9.83 | -1 | -1 | -1 | -1 | 381.04 | 760 | 17:13:20 | 2.1 | 760 | 0 | 0 | 0 | 17.9217 | 24.74 | 6.8183 | 9.8973 | 10.2585 | 10.4905 | 78.57 | 10.0669 | 0 | 0 | 0.22259 | 0.33261 | 615 | 0.29025 | 0.34249 | 395 | 0.18642 | 0.21997 | 172.2921 | 257.4493 | 587.516 | 877.9023 | 2349.2378 | 8010.9007 | 0 | 0 | 0 | 0 | 8010.9007 | 8888.803 | 10.5407 | 11.6958 | 749.2 | 8023.4331 | 10.7121 | 0
| 17:13:30 | 24.67 | 35.41 | 23.7 | 18.69 | 18.03 | 17.76 | 17.26 | 16.98 | 18.83 | 19.06 | 17.53 | 13.45 | 12.11 | 65.66 | 41.73 | 40.57 | 149.46 | 369.17 | 54.39 | 52.49 | 28.96 | 76.46 | 80.78 | 69.84 | 0 | 0 | 10.22 | 10.45 | 9.99 | 9.84 | -1 | -1 | -1 | -1 | 381.04 | 760 | 17:13:30 | 2.2667 | 760 | 0 | 0 | 0 | 17.925 | 24.67 | 6.745 | 9.9442 | 10.1755 | 10.4043 | 78.62 | 10.0756 | 0 | 0 | 0.13101 | 0.32395 | 615 | 0.29025 | 0.34249 | 395 | 0.18642 | 0.21997 | 101.4024 | 250.7476 | 345.7821 | 855.0492 | 2323.971 | 7924.741 | 0 | 0 | 0 | 0 | 7924.741 | 8779.7902 | 10.4273 | 11.5524 | 754.8 | 8012.8589 | 10.6179 | 0
| 17:13:42 | 24.76 | 35.46 | 23.93 | 18.69 | 18 | 17.79 | 17.33 | 16.99 | 18.85 | 19.07 | 17.23 | 13.44 | 12.13 | 65.79 | 41.82 | 40.57 | 149.71 | 369.18 | 54.4 | 52.49 | 28.97 | 76.56 | 80.79 | 69.94 | 0 | 0 | 10.28 | 10.49 | 10.13 | 9.86 | -1 | -1 | -1 | -1 | 381.04 | 741 | 17:13:42 | 2.4667 | 741 | 0 | 0 | 0 | 17.9417 | 24.76 | 6.8183 | 10.0869 | 10.2313 | 10.4372 | 78.675 | 10.0935 | 0 | 0 | 0.16885 | 0.30603 | 615 | 0.29025 | 0.34249 | 395 | 0.18642 | 0.21997 | 130.6961 | 236.8788 | 445.6738 | 807.7566 | 2349.2378 | 8010.9007 | 0 | 0 | 0 | 0 | 8010.9007 | 8818.6574 | 10.8109 | 11.901 | 755 | 7983.8779 | 10.5758 | 0
| 17:13:53 | 24.7 | 35.52 | 23.76 | 18.65 | 18.05 | 17.82 | 17.33 | 17.01 | 18.88 | 19.05 | 17.03 | 13.48 | 12.13 | 65.87 | 41.84 | 40.58 | 149.11 | 370.39 | 54.39 | 52.49 | 28.53 | 76.56 | 80.79 | 70.25 | 0 | 0 | 10.24 | 10.36 | 10.03 | 9.88 | -1 | -1 | -1 | -1 | 381.05 | 742 | 17:13:53 | 2.65 | 742 | 0 | 0 | 0 | 17.9567 | 24.7 | 6.7433 | 9.9808 | 10.1941 | 10.3106 | 78.675 | 10.1032 | 0 | 0 | 0.12196 | 0.29634 | 615 | 0.29025 | 0.34249 | 395 | 0.18642 | 0.21997 | 94.3989 | 229.3799 | 321.9002 | 782.1854 | 2323.3967 | 7922.7828 | 0 | 0 | 0 | 0 | 7922.7828 | 8704.9682 | 10.6776 | 11.7318 | 752.2 | 7985.0528 | 10.6169 | 0
| 17:14:04 | 24.91 | 35.58 | 24.01 | 18.71 | 18.06 | 17.78 | 17.26 | 16.96 | 18.89 | 19.08 | 17.2 | 13.5 | 12.12 | 65.93 | 41.96 | 40.71 | 149.6 | 370.65 | 54.18 | 52.49 | 28.53 | 76.56 | 80.79 | 70.25 | 0 | 0 | 10.37 | 10.4 | 10.14 | 9.87 | -1 | -1 | -1 | -1 | 381.05 | 764 | 17:14:04 | 2.8333 | 764 | 0 | 0 | 0 | 17.9433 | 24.91 | 6.9667 | 10.0946 | 10.3248 | 10.3453 | 78.675 | 10.0945 | 0 | 0 | 0.26132 | 0.30496 | 615 | 0.29025 | 0.34249 | 395 | 0.18642 | 0.21997 | 202.2692 | 236.0459 | 689.738 | 804.9165 | 2400.3456 | 8185.1785 | 0 | 0 | 0 | 0 | 8185.1785 | 8990.0949 | 10.7136 | 11.7671 | 753.4 | 8010.9007 | 10.634 | 0
| 17:14:15 | 24.87 | 35.69 | 23.84 | 18.73 | 18.06 | 17.85 | 17.33 | 17.02 | 18.87 | 19.08 | 17.15 | 13.61 | 12.17 | 66.02 | 42.06 | 40.64 | 149.34 | 371.81 | 54.4 | 52.7 | 28.43 | 76.76 | 81.11 | 70.45 | 0 | 0 | 10.39 | 10.42 | 10.08 | 9.92 | -1 | -1 | -1 | -1 | 381.05 | 764 | 17:14:15 | 3.0167 | 764 | 0 | 0 | 0 | 17.9767 | 24.87 | 6.8933 | 10.0316 | 10.3417 | 10.3721 | 78.935 | 10.1501 | 0 | 0 | 0.22267 | 0.24944 | 615 | 0.29025 | 0.34249 | 395 | 0.18642 | 0.21997 | 172.356 | 193.0724 | 587.7341 | 658.3768 | 2375.0788 | 8099.0187 | 0 | 0 | 0 | 0 | 8099.0187 | 8757.3955 | 10.6008 | 11.4626 | 754.2 | 8028.5243 | 10.646 | 0
| 17:14:27 | 24.84 | 35.77 | 23.8 | 18.82 | 18.03 | 17.85 | 17.38 | 17.04 | 18.91 | 19.1 | 17.26 | 13.53 | 12.21 | 66.09 | 42.13 | 40.85 | 149.63 | 373.04 | 54.4 | 52.5 | 28.32 | 76.76 | 81 | 70.55 | 0 | 0 | 10.33 | 10.43 | 10.05 | 9.94 | -1 | -1 | -1 | -1 | 381.05 | 747 | 17:14:27 | 3.2167 | 747 | 0 | 0 | 0 | 18.005 | 24.84 | 6.835 | 10.0071 | 10.2831 | 10.3776 | 78.88 | 10.1613 | 0 | 0 | 0.15284 | 0.23823 | 615 | 0.29025 | 0.34249 | 395 | 0.18642 | 0.21997 | 118.3012 | 184.3993 | 403.4072 | 628.8015 | 2354.9802 | 8030.4825 | 0 | 0 | 0 | 0 | 8030.4825 | 8659.284 | 10.7503 | 11.5921 | 751.6 | 8049.6726 | 10.7106 | 0
| 17:14:38 | 24.75 | 35.89 | 23.93 | 18.72 | 18.02 | 17.85 | 17.37 | 17.02 | 18.9 | 19.09 | 16.95 | 13.54 | 12.2 | 66.14 | 42.24 | 40.99 | 149.86 | 373.3 | 54.19 | 52.28 | 28 | 76.66 | 81.11 | 70.45 | 0 | 0 | 10.23 | 10.38 | 10.1 | 9.92 | -1 | -1 | -1 | -1 | 381.05 | 747 | 17:14:38 | 3.4 | 747 | 0 | 0 | 0 | 17.98 | 24.75 | 6.77 | 10.0473 | 10.1835 | 10.3275 | 78.885 | 10.1457 | 0 | 0 | 0.06884 | 0.25381 | 615 | 0.29025 | 0.34249 | 395 | 0.18642 | 0.21997 | 53.2847 | 196.4563 | 181.7009 | 669.9159 | 2332.5846 | 7954.1136 | 0 | 0 | 0 | 0 | 7954.1136 | 8624.0295 | 10.6481 | 11.5449 | 752.8 | 8038.3152 | 10.6781 | 0
| 17:14:48 | 24.79 | 35.91 | 24.04 | 18.66 | 18.09 | 17.82 | 17.32 | 17.03 | 18.87 | 19.1 | 16.76 | 13.45 | 12.18 | 66.19 | 42.25 | 41.11 | 149.43 | 374.2 | 54.2 | 52.7 | 27.88 | 76.76 | 81.01 | 70.55 | 0 | 0 | 10.34 | 10.34 | 10.16 | 9.92 | -1 | -1 | -1 | -1 | 381.06 | 768 | 17:14:48 | 3.5667 | 768 | 0 | 0 | 0 | 17.965 | 24.79 | 6.825 | 10.1169 | 10.2916 | 10.294 | 78.885 | 10.136 | 0 | 0 | 0.18669 | 0.26354 | 615 | 0.29025 | 0.34249 | 395 | 0.18642 | 0.21997 | 144.504 | 203.9859 | 492.7585 | 695.5919 | 2351.5347 | 8018.7334 | 0 | 0 | 0 | 0 | 8018.7334 | 8714.3253 | 10.4411 | 11.3468 | 758 | 8057.5053 | 10.6308 | 0
| 17:14:59 | 24.89 | 35.96 | 24.02 | 18.72 | 18.07 | 17.82 | 17.34 | 17.02 | 18.85 | 19.1 | 16.88 | 13.48 | 12.19 | 66.23 | 42.31 | 41.12 | 150.39 | 374.68 | 53.99 | 52.38 | 27.66 | 76.56 | 80.8 | 70.34 | 0 | 0 | 10.33 | 10.29 | 10.11 | 9.89 | -1 | -1 | -1 | -1 | 381.06 | 769 | 17:14:59 | 3.75 | 769 | 0 | 0 | 0 | 17.97 | 24.89 | 6.92 | 10.0648 | 10.2904 | 10.2399 | 78.68 | 10.1124 | 0 | 0 | 0.20895 | 0.28707 | 615 | 0.29025 | 0.34249 | 395 | 0.18642 | 0.21997 | 161.7342 | 222.2033 | 551.5138 | 757.7132 | 2384.2667 | 8130.3495 | 0 | 0 | 0 | 0 | 8130.3495 | 8888.0627 | 10.5726 | 11.5579 | 759 | 8046.5395 | 10.6026 | 0
| 17:15:09 | 24.73 | 35.99 | 23.88 | 18.66 | 18.11 | 17.85 | 17.36 | 17.04 | 18.83 | 19.07 | 16.81 | 13.55 | 12.21 | 66.32 | 42.35 | 41.14 | 150 | 375.12 | 53.99 | 52.49 | 27.67 | 76.76 | 81.01 | 70.54 | 0 | 0 | 10.26 | 10.31 | 10.03 | 9.92 | -1 | -1 | -1 | -1 | 381.06 | 770 | 17:15:09 | 3.9167 | 770 | 0 | 0 | 0 | 17.975 | 24.73 | 6.755 | 9.9791 | 10.2127 | 10.2609 | 78.885 | 10.1425 | 0 | 0 | 0.10125 | 0.25705 | 615 | 0.29025 | 0.34249 | 395 | 0.18642 | 0.21997 | 78.3734 | 198.9669 | 267.2532 | 678.477 | 2327.4164 | 7936.49 | 0 | 0 | 0 | 0 | 7936.49 | 8614.967 | 10.3071 | 11.1883 | 760.2 | 8014.0338 | 10.5438 | 0
| 17:15:20 | 24.84 | 36.05 | 24.09 | 18.74 | 18.07 | 17.88 | 17.38 | 17.03 | 18.89 | 19.12 | 16.81 | 13.54 | 12.25 | 66.4 | 42.4 | 41.2 | 149.7 | 375.19 | 53.99 | 52.6 | 27.67 | 76.87 | 81.02 | 70.64 | 0 | 0 | 10.35 | 10.34 | 10.15 | 9.95 | -1 | -1 | -1 | -1 | 381.07 | 772 | 17:15:20 | 4.1 | 772 | 0 | 0 | 0 | 17.9983 | 24.84 | 6.8417 | 10.1079 | 10.303 | 10.2953 | 78.945 | 10.1654 | 0 | 0 | 0.16857 | 0.23406 | 615 | 0.29025 | 0.34249 | 395 | 0.18642 | 0.21997 | 130.4808 | 181.1668 | 444.9395 | 617.7789 | 2357.2772 | 8038.3152 | 0 | 0 | 0 | 0 | 8038.3152 | 8656.0941 | 10.4123 | 11.2126 | 765.2 | 8015.6004 | 10.4762 | 0
| 17:15:30 | 24.8 | 36.12 | 23.98 | 18.66 | 18.08 | 17.85 | 17.38 | 17.02 | 18.93 | 19.11 | 16.69 | 13.48 | 12.22 | 66.44 | 42.47 | 41.34 | 149.47 | 375.43 | 53.79 | 52.6 | 27.23 | 76.76 | 80.92 | 70.76 | 0 | 0 | 10.32 | 10.22 | 10.04 | 9.94 | -1 | -1 | -1 | -1 | 381.07 | 772 | 17:15:30 | 4.2667 | 772 | 0 | 0 | 0 | 17.9867 | 24.8 | 6.8133 | 10.0025 | 10.278 | 10.1685 | 78.84 | 10.1441 | 0 | 0 | 0.16491 | 0.25537 | 615 | 0.29025 | 0.34249 | 395 | 0.18642 | 0.21997 | 127.6421 | 197.6625 | 435.2597 | 674.0292 | 2347.515 | 8005.0262 | 0 | 0 | 0 | 0 | 8005.0262 | 8679.0554 | 10.3692 | 11.2423 | 770.2 | 8025.7829 | 10.4205 | 0
| 17:15:40 | 24.92 | 36.21 | 24.04 | 18.64 | 18.11 | 17.9 | 17.37 | 17.07 | 18.97 | 19.17 | 16.69 | 13.58 | 12.26 | 66.49 | 42.55 | 41.34 | 149.94 | 376.66 | 54.01 | 52.49 | 27.23 | 76.77 | 81.02 | 70.76 | 0 | 0 | 10.38 | 10.27 | 10.12 | 9.96 | -1 | -1 | -1 | -1 | 381.07 | 774 | 17:15:40 | 4.4333 | 774 | 0 | 0 | 0 | 18.01 | 24.92 | 6.91 | 10.0809 | 10.3311 | 10.2197 | 78.895 | 10.1665 | 0 | 0 | 0.19564 | 0.23302 | 615 | 0.29025 | 0.34249 | 395 | 0.18642 | 0.21997 | 151.4352 | 180.3639 | 516.3941 | 615.0411 | 2380.8212 | 8118.6004 | 0 | 0 | 0 | 0 | 8118.6004 | 8733.6415 | 10.4891 | 11.2838 | 771.4 | 8045.7563 | 10.4301 | 0
| 17:15:51 | 25.02 | 36.22 | 23.96 | 18.72 | 18.14 | 17.91 | 17.4 | 17.03 | 18.95 | 19.16 | 16.6 | 13.59 | 12.31 | 66.53 | 42.58 | 41.4 | 149.53 | 377.49 | 54 | 52.91 | 27.23 | 77.17 | 81.32 | 70.76 | 0 | 0 | 10.52 | 10.28 | 10.08 | 10 | -1 | -1 | -1 | -1 | 381.07 | 773 | 17:15:51 | 4.6167 | 773 | 0 | 0 | 0 | 18.025 | 25.02 | 6.995 | 10.0299 | 10.4785 | 10.2254 | 79.245 | 10.2221 | 0 | 0 | 0.28739 | 0.17738 | 615 | 0.29025 | 0.34249 | 395 | 0.18642 | 0.21997 | 222.4502 | 137.2962 | 758.555 | 468.1802 | 2410.1078 | 8218.4675 | 0 | 0 | 0 | 0 | 8218.4675 | 8686.6476 | 10.6319 | 11.2376 | 772.2 | 8063.3799 | 10.4419 | 0
| 17:16:03 | 25.04 | 36.25 | 24.12 | 18.7 | 18.13 | 17.87 | 17.49 | 17.17 | 18.94 | 19.16 | 17.17 | 13.6 | 12.28 | 66.59 | 42.64 | 41.45 | 149.82 | 377.41 | 54.21 | 52.91 | 27.24 | 76.87 | 81.11 | 70.76 | 0 | 0 | 10.54 | 10.3 | 10.22 | 9.99 | -1 | -1 | -1 | -1 | 381.08 | 775 | 17:16:03 | 4.8167 | 775 | 0 | 0 | 0 | 18.05 | 25.04 | 6.99 | 10.1683 | 10.4912 | 10.2463 | 78.99 | 10.205 | 0 | 0 | 0.31724 | 0.19451 | 615 | 0.29025 | 0.34249 | 395 | 0.18642 | 0.21997 | 245.5515 | 150.5605 | 837.3306 | 513.4115 | 2408.385 | 8212.5929 | 0 | 0 | 0 | 0 | 8212.5929 | 8726.0044 | 10.5969 | 11.2594 | 773.2 | 8118.6004 | 10.4999 | 0
| 17:16:14 | 24.89 | 36.27 | 24.03 | 18.86 | 18.16 | 17.91 | 17.46 | 17.13 | 19 | 19.19 | 17.06 | 13.59 | 12.3 | 66.62 | 42.72 | 41.47 | 150.51 | 377.4 | 54.01 | 53.12 | 27.02 | 77.07 | 81.23 | 70.76 | 0 | 0 | 10.48 | 10.23 | 10.12 | 10.03 | -1 | -1 | -1 | -1 | 381.08 | 775 | 17:16:14 | 5 | 775 | 0 | 0 | 0 | 18.0867 | 24.89 | 6.8033 | 10.0747 | 10.4382 | 10.1735 | 79.15 | 10.25 | 0 | 0 | 0.21921 | 0.14951 | 615 | 0.29025 | 0.34249 | 395 | 0.18642 | 0.21997 | 169.6727 | 115.7264 | 578.5839 | 394.6271 | 2344.0695 | 7993.2771 | 0 | 0 | 0 | 0 | 7993.2771 | 8387.9042 | 10.3139 | 10.8231 | 773.8 | 8109.5928 | 10.4802 | 0
| 17:16:24 | 25.1 | 36.36 | 24.03 | 18.93 | 18.09 | 17.93 | 17.42 | 17.09 | 18.98 | 19.21 | 17.12 | 13.62 | 12.3 | 66.59 | 42.74 | 41.67 | 150.47 | 378.18 | 54.21 | 52.92 | 27.02 | 77.07 | 81.22 | 70.96 | 0 | 0 | 10.58 | 10.27 | 10.16 | 10.03 | -1 | -1 | -1 | -1 | 381.08 | 775 | 17:16:24 | 5.1667 | 775 | 0 | 0 | 0 | 18.0733 | 25.1 | 7.0267 | 10.1126 | 10.5314 | 10.2246 | 79.145 | 10.2406 | 0 | 0 | 0.32185 | 0.1589 | 615 | 0.29025 | 0.34249 | 395 | 0.18642 | 0.21997 | 249.1254 | 122.993 | 849.5175 | 419.4063 | 2421.0184 | 8255.6728 | 0 | 0 | 0 | 0 | 8255.6728 | 8675.0791 | 10.6525 | 11.1937 | 774.4 | 8159.7222 | 10.5369 | 0
| 17:16:35 | 24.95 | 36.49 | 24.04 | 18.78 | 18.21 | 17.95 | 17.46 | 17.1 | 18.96 | 19.23 | 17.52 | 13.65 | 12.33 | 66.7 | 42.82 | 41.6 | 150.35 | 379.48 | 54.11 | 52.93 | 27.02 | 77.07 | 81.23 | 70.96 | 0 | 0 | 10.49 | 10.35 | 10.15 | 10.03 | -1 | -1 | -1 | -1 | 381.08 | 776 | 17:16:35 | 5.35 | 776 | 0 | 0 | 0 | 18.0767 | 24.95 | 6.8733 | 10.0999 | 10.4381 | 10.2988 | 79.15 | 10.2434 | 0 | 0 | 0.22571 | 0.15606 | 615 | 0.29025 | 0.34249 | 395 | 0.18642 | 0.21997 | 174.7071 | 120.7951 | 595.7512 | 411.9114 | 2368.1878 | 8075.5206 | 0 | 0 | 0 | 0 | 8075.5206 | 8487.4319 | 10.4066 | 10.9374 | 774.8 | 8151.1062 | 10.5204 | 0
| 17:16:46 | 24.95 | 36.56 | 24.03 | 18.83 | 18.21 | 17.9 | 17.41 | 17.07 | 18.98 | 19.25 | 17.5 | 13.65 | 12.31 | 66.76 | 42.9 | 41.71 | 150.19 | 380.29 | 54.02 | 52.72 | 26.81 | 76.77 | 81.02 | 70.86 | 0 | 0 | 10.44 | 10.31 | 10.12 | 10 | -1 | -1 | -1 | -1 | 381.08 | 778 | 17:16:46 | 5.5333 | 778 | 0 | 0 | 0 | 18.0667 | 24.95 | 6.8833 | 10.0766 | 10.396 | 10.2573 | 78.895 | 10.2034 | 0 | 0 | 0.22367 | 0.19613 | 615 | 0.29025 | 0.34249 | 395 | 0.18642 | 0.21997 | 173.1286 | 151.8077 | 590.3686 | 517.6644 | 2371.6333 | 8087.2696 | 0 | 0 | 0 | 0 | 8087.2696 | 8604.934 | 10.3949 | 11.0603 | 775.8 | 8124.8666 | 10.473 | 0
| 17:16:58 | 24.93 | 36.57 | 24.04 | 18.73 | 18.23 | 17.97 | 17.49 | 17.09 | 18.99 | 19.23 | 17.11 | 13.68 | 12.38 | 66.85 | 42.94 | 41.88 | 150.59 | 380.03 | 53.91 | 52.82 | 26.81 | 76.98 | 81.23 | 70.86 | 0 | 0 | 10.45 | 10.32 | 10.11 | 10.03 | -1 | -1 | -1 | -1 | 381.09 | 780 | 17:16:58 | 5.7333 | 780 | 0 | 0 | 0 | 18.0833 | 24.93 | 6.8467 | 10.0619 | 10.4034 | 10.263 | 79.105 | 10.2419 | 0 | 0 | 0.19259 | 0.15762 | 615 | 0.29025 | 0.34249 | 395 | 0.18642 | 0.21997 | 149.0681 | 122.0003 | 508.3223 | 416.0211 | 2358.9999 | 8044.1897 | 0 | 0 | 0 | 0 | 8044.1897 | 8460.2108 | 10.3131 | 10.8464 | 776.8 | 8091.186 | 10.4162 | 0
| 17:17:08 | 25.03 | 36.55 | 24.04 | 18.85 | 18.2 | 17.95 | 17.44 | 17.09 | 19.09 | 19.23 | 16.96 | 13.63 | 12.35 | 66.92 | 42.94 | 41.91 | 150.28 | 379.89 | 54.03 | 52.93 | 26.6 | 76.98 | 81.13 | 70.87 | 0 | 0 | 10.54 | 10.22 | 10.13 | 10.03 | -1 | -1 | -1 | -1 | 381.09 | 780 | 17:17:08 | 5.9 | 780 | 0 | 0 | 0 | 18.1033 | 25.03 | 6.9267 | 10.0847 | 10.4889 | 10.17 | 79.055 | 10.2484 | 0 | 0 | 0.2715 | 0.15111 | 615 | 0.29025 | 0.34249 | 395 | 0.18642 | 0.21997 | 210.1525 | 116.962 | 716.6201 | 398.8403 | 2386.5637 | 8138.1822 | 0 | 0 | 0 | 0 | 8138.1822 | 8537.0225 | 10.4336 | 10.9449 | 777.8 | 8120.167 | 10.4401 | 0
| 17:17:18 | 25.07 | 36.57 | 24.05 | 18.81 | 18.16 | 17.94 | 17.47 | 17.09 | 19.08 | 19.24 | 17.3 | 13.73 | 12.35 | 67 | 42.95 | 41.68 | 150.31 | 380.93 | 53.61 | 52.73 | 26.48 | 76.98 | 81.23 | 70.77 | 0 | 0 | 10.52 | 10.19 | 10.05 | 10.03 | -1 | -1 | -1 | -1 | 381.09 | 779 | 17:17:18 | 6.0667 | 779 | 0 | 0 | 0 | 18.0917 | 25.07 | 6.9783 | 10.0111 | 10.4739 | 10.1346 | 79.105 | 10.2473 | 0 | 0 | 0.25761 | 0.15216 | 615 | 0.29025 | 0.34249 | 395 | 0.18642 | 0.21997 | 199.4015 | 117.7775 | 679.959 | 401.6212 | 2404.3653 | 8198.8857 | 0 | 0 | 0 | 0 | 8198.8857 | 8600.5069 | 10.5249 | 11.0404 | 778.6 | 8108.8096 | 10.4146 | 0
| 17:17:29 | 25.05 | 36.59 | 24.18 | 18.94 | 18.24 | 17.96 | 17.46 | 17.11 | 19.16 | 19.26 | 17.49 | 13.68 | 12.32 | 67.04 | 42.99 | 41.74 | 150.31 | 381.4 | 54.03 | 52.73 | 26.6 | 77.19 | 81.45 | 70.98 | 0 | 0 | 10.51 | 10.25 | 10.22 | 10.09 | -1 | -1 | -1 | -1 | 381.1 | 780 | 17:17:29 | 6.25 | 780 | 0 | 0 | 0 | 18.145 | 25.05 | 6.905 | 10.1712 | 10.4612 | 10.1926 | 79.32 | 10.3107 | 0 | 0 | 0.18154 | 0.088773 | 615 | 0.29025 | 0.34249 | 395 | 0.18642 | 0.21997 | 140.5192 | 68.7136 | 479.1706 | 234.3133 | 2379.0985 | 8112.7259 | 0 | 0 | 0 | 0 | 8112.7259 | 8347.0392 | 10.4009 | 10.7013 | 779.4 | 8116.2506 | 10.4135 | 0
| 17:17:39 | 25.19 | 36.72 | 24.17 | 18.84 | 18.21 | 17.99 | 17.42 | 17.07 | 19.03 | 19.31 | 17.59 | 13.66 | 12.38 | 67.11 | 43.05 | 41.91 | 150.35 | 381.67 | 53.82 | 52.32 | 26.38 | 76.79 | 81.03 | 70.88 | 0 | 0 | 10.51 | 10.23 | 10.17 | 10.03 | -1 | -1 | -1 | -1 | 381.1 | 780 | 17:17:39 | 6.4167 | 780 | 0 | 0 | 0 | 18.0933 | 25.19 | 7.0967 | 10.1248 | 10.4669 | 10.1802 | 78.91 | 10.2228 | 0 | 0 | 0.27518 | 0.17675 | 615 | 0.29025 | 0.34249 | 395 | 0.18642 | 0.21997 | 213.0003 | 136.8086 | 726.3311 | 466.5173 | 2445.1367 | 8337.9162 | 0 | 0 | 0 | 0 | 8337.9162 | 8804.4336 | 10.6896 | 11.2877 | 779.8 | 8166.38 | 10.4724 | 0
| 17:17:50 | 25.1 | 36.76 | 24.25 | 18.81 | 18.25 | 17.97 | 17.43 | 17.07 | 19 | 19.28 | 17.51 | 13.62 | 12.37 | 67.18 | 43.13 | 41.93 | 150.44 | 381.63 | 53.83 | 52.94 | 26.39 | 76.89 | 81.23 | 70.78 | 0 | 0 | 10.58 | 10.26 | 10.22 | 10.03 | -1 | -1 | -1 | -1 | 381.1 | 781 | 17:17:50 | 6.6 | 781 | 0 | 0 | 0 | 18.0883 | 25.1 | 7.0117 | 10.1762 | 10.5355 | 10.2067 | 79.06 | 10.2392 | 0 | 0 | 0.32727 | 0.16027 | 615 | 0.29025 | 0.34249 | 395 | 0.18642 | 0.21997 | 253.3175 | 124.0523 | 863.8127 | 423.0182 | 2415.8502 | 8238.0492 | 0 | 0 | 0 | 0 | 8238.0492 | 8661.0674 | 10.5481 | 11.0897 | 780 | 8205.1519 | 10.5194 | 0
| 17:18:03 | 25.06 | 36.83 | 24.36 | 18.9 | 18.24 | 17.97 | 17.44 | 17.12 | 19.06 | 19.27 | 17.35 | 13.76 | 12.41 | 67.21 | 43.17 | 42.04 | 150.58 | 382.03 | 53.62 | 52.42 | 26.38 | 76.79 | 81.22 | 70.78 | 0 | 0 | 10.45 | 10.29 | 10.25 | 10.04 | -1 | -1 | -1 | -1 | 381.1 | 783 | 17:18:03 | 6.8167 | 783 | 0 | 0 | 0 | 18.1217 | 25.06 | 6.9383 | 10.204 | 10.405 | 10.2425 | 79.005 | 10.2538 | 0 | 0 | 0.18223 | 0.14569 | 615 | 0.29025 | 0.34249 | 395 | 0.18642 | 0.21997 | 141.0538 | 112.7703 | 480.9933 | 384.5468 | 2390.5834 | 8151.8895 | 0 | 0 | 0 | 0 | 8151.8895 | 8536.4363 | 10.4111 | 10.9022 | 780.6 | 8207.8933 | 10.5149 | 0
| 17:18:16 | 25.18 | 36.81 | 24.5 | 18.93 | 18.33 | 18.04 | 17.53 | 17.16 | 19.14 | 19.34 | 17.14 | 13.78 | 12.49 | 67.28 | 43.2 | 41.99 | 151.1 | 382.8 | 53.63 | 52.53 | 26.16 | 77 | 81.45 | 70.88 | 0 | 0 | 10.55 | 10.19 | 10.34 | 10.11 | -1 | -1 | -1 | -1 | 381.1 | 783 | 17:18:16 | 7.0333 | 783 | 0 | 0 | 0 | 18.1883 | 25.18 | 6.9917 | 10.2933 | 10.5033 | 10.1444 | 79.225 | 10.3267 | 0 | 0 | 0.20758 | 0.072784 | 615 | 0.29025 | 0.34249 | 395 | 0.18642 | 0.21997 | 160.674 | 56.3374 | 547.8984 | 192.1105 | 2408.9593 | 8214.5511 | 0 | 0 | 0 | 0 | 8214.5511 | 8406.6616 | 10.4911 | 10.7365 | 781.4 | 8211.0264 | 10.5082 | 0
| 17:18:27 | 25.13 | 36.77 | 24.38 | 18.93 | 18.38 | 18.12 | 17.64 | 17.22 | 19.15 | 19.35 | 17.15 | 13.85 | 12.51 | 67.38 | 43.19 | 42.04 | 152.08 | 382.99 | 54.05 | 52.94 | 26.39 | 77.2 | 81.66 | 71.18 | 0 | 0 | 10.61 | 10.26 | 10.34 | 10.17 | -1 | -1 | -1 | -1 | 381.11 | 781 | 17:18:27 | 7.2167 | 781 | 0 | 0 | 0 | 18.24 | 25.13 | 6.89 | 10.2997 | 10.5546 | 10.2124 | 79.43 | 10.3881 | 0 | 0 | 0.19757 | 0.011403 | 615 | 0.29025 | 0.34249 | 395 | 0.18642 | 0.21997 | 152.9236 | 8.8263 | 521.4696 | 30.0976 | 2373.9303 | 8095.1023 | 0 | 0 | 0 | 0 | 8095.1023 | 8125.2 | 10.365 | 10.4036 | 781.6 | 8207.5017 | 10.501 | 0
| 17:18:37 | 25.05 | 36.82 | 24.24 | 18.87 | 18.4 | 18.12 | 17.56 | 17.15 | 19.06 | 19.35 | 17.24 | 13.81 | 12.48 | 67.36 | 43.21 | 42.07 | 150.93 | 382.79 | 54.26 | 52.73 | 26.4 | 77.22 | 81.66 | 71.19 | 0 | 0 | 10.51 | 10.29 | 10.3 | 10.14 | -1 | -1 | -1 | -1 | 381.11 | 783 | 17:18:37 | 7.3833 | 783 | 0 | 0 | 0 | 18.1933 | 25.05 | 6.8567 | 10.2526 | 10.4612 | 10.2447 | 79.44 | 10.3585 | 0 | 0 | 0.13375 | 0.040986 | 615 | 0.29025 | 0.34249 | 395 | 0.18642 | 0.21997 | 103.5301 | 31.7245 | 353.0377 | 108.1804 | 2362.4454 | 8055.9388 | 0 | 0 | 0 | 0 | 8055.9388 | 8164.1192 | 10.2886 | 10.4267 | 782.2 | 8151.1062 | 10.4208 | 0
| 17:18:48 | 24.93 | 36.94 | 24.23 | 18.97 | 18.32 | 18.08 | 17.58 | 17.2 | 19.19 | 19.4 | 17.39 | 13.76 | 12.49 | 67.43 | 43.26 | 42.16 | 151.18 | 384 | 54.05 | 52.73 | 26.28 | 77.01 | 81.46 | 71.28 | 0 | 0 | 10.43 | 10.31 | 10.25 | 10.15 | -1 | -1 | -1 | -1 | 381.11 | 786 | 17:18:48 | 7.5667 | 786 | 0 | 0 | 0 | 18.2233 | 24.93 | 6.7067 | 10.2061 | 10.3854 | 10.2654 | 79.235 | 10.3512 | 0 | 0 | 0.065298 | 0.048351 | 615 | 0.29025 | 0.34249 | 395 | 0.18642 | 0.21997 | 50.543 | 37.4251 | 172.3515 | 127.6196 | 2310.7633 | 7879.7029 | 0 | 0 | 0 | 0 | 7879.7029 | 8007.3225 | 10.0251 | 10.1874 | 783.2 | 8079.4369 | 10.3162 | 0
| 17:18:59 | 25.05 | 36.91 | 24.19 | 19.04 | 18.32 | 18.07 | 17.5 | 17.17 | 19.15 | 19.37 | 17.16 | 13.87 | 12.45 | 67.51 | 43.32 | 42.29 | 150.28 | 383.43 | 53.63 | 52.32 | 25.95 | 76.81 | 81.25 | 70.79 | 0 | 0 | 10.42 | 10.17 | 10.14 | 10.1 | -1 | -1 | -1 | -1 | 381.11 | 785 | 17:18:59 | 7.75 | 785 | 0 | 0 | 0 | 18.2083 | 25.05 | 6.8417 | 10.1008 | 10.3785 | 10.1176 | 79.03 | 10.314 | 0 | 0 | 0.095529 | 0.085459 | 615 | 0.29025 | 0.34249 | 395 | 0.18642 | 0.21997 | 73.9425 | 66.1481 | 252.144 | 225.5649 | 2357.2772 | 8038.3152 | 0 | 0 | 0 | 0 | 8038.3152 | 8263.8801 | 10.2399 | 10.5272 | 783.6 | 8056.7221 | 10.2819 | 0
| 17:19:09 | 25.15 | 37.09 | 24.39 | 19.07 | 18.31 | 18.07 | 17.54 | 17.19 | 19.13 | 19.38 | 17.34 | 13.77 | 12.45 | 67.64 | 43.45 | 42.26 | 150.63 | 385.47 | 53.64 | 52.53 | 25.95 | 76.81 | 81.25 | 70.8 | 0 | 0 | 10.53 | 10.27 | 10.27 | 10.11 | -1 | -1 | -1 | -1 | 381.11 | 787 | 17:19:09 | 7.9167 | 787 | 0 | 0 | 0 | 18.2183 | 25.15 | 6.9317 | 10.2266 | 10.4842 | 10.219 | 79.03 | 10.3206 | 0 | 0 | 0.19461 | 0.078871 | 615 | 0.29025 | 0.34249 | 395 | 0.18642 | 0.21997 | 150.6326 | 61.0491 | 513.6572 | 208.1774 | 2388.2864 | 8144.0567 | 0 | 0 | 0 | 0 | 8144.0567 | 8352.2341 | 10.3482 | 10.6127 | 784.4 | 8042.6232 | 10.2534 | 0
| 17:19:19 | 25.12 | 37 | 24.17 | 18.97 | 18.37 | 18.07 | 17.56 | 17.19 | 19.11 | 19.34 | 17.4 | 13.83 | 12.48 | 67.69 | 43.38 | 42.29 | 151.09 | 384.95 | 53.64 | 52.63 | 25.96 | 76.82 | 81.25 | 70.9 | 0 | 0 | 10.53 | 10.22 | 10.13 | 10.1 | -1 | -1 | -1 | -1 | 381.11 | 786 | 17:19:19 | 8.0833 | 786 | 0 | 0 | 0 | 18.2117 | 25.12 | 6.9083 | 10.0904 | 10.4854 | 10.1722 | 79.035 | 10.3169 | 0 | 0 | 0.19957 | 0.0826 | 615 | 0.29025 | 0.34249 | 395 | 0.18642 | 0.21997 | 154.4699 | 63.9352 | 526.7424 | 218.0189 | 2380.247 | 8116.6423 | 0 | 0 | 0 | 0 | 8116.6423 | 8334.6612 | 10.3265 | 10.6039 | 785.4 | 8046.9312 | 10.2457 | 0
| 17:19:30 | 24.96 | 37.06 | 24.22 | 18.99 | 18.39 | 18.1 | 17.57 | 17.18 | 19.16 | 19.41 | 17.43 | 13.81 | 12.48 | 67.75 | 43.42 | 42.21 | 150.96 | 385.18 | 53.64 | 52.53 | 25.96 | 76.81 | 81.25 | 71 | 0 | 0 | 10.41 | 10.26 | 10.17 | 10.13 | -1 | -1 | -1 | -1 | 381.12 | 786 | 17:19:30 | 8.2667 | 786 | 0 | 0 | 0 | 18.2317 | 24.96 | 6.7283 | 10.1212 | 10.3642 | 10.206 | 79.03 | 10.3294 | 0 | 0 | 0.065819 | 0.070082 | 615 | 0.29025 | 0.34249 | 395 | 0.18642 | 0.21997 | 50.9457 | 54.2459 | 173.7247 | 184.9785 | 2318.2285 | 7905.1592 | 0 | 0 | 0 | 0 | 7905.1592 | 8090.1377 | 10.0575 | 10.2928 | 786 | 8016.7753 | 10.1994 | 0
| 17:19:40 | 25.22 | 37.08 | 24.27 | 18.96 | 18.38 | 18.11 | 17.56 | 17.2 | 19.12 | 19.4 | 17.57 | 13.86 | 12.5 | 67.77 | 43.42 | 42.38 | 151.11 | 385.01 | 53.64 | 52.54 | 25.85 | 76.82 | 81.25 | 70.99 | 0 | 0 | 10.58 | 10.22 | 10.2 | 10.12 | -1 | -1 | -1 | -1 | 381.12 | 785 | 17:19:40 | 8.4333 | 785 | 0 | 0 | 0 | 18.2217 | 25.22 | 6.9983 | 10.1521 | 10.5308 | 10.1733 | 79.035 | 10.3235 | 0 | 0 | 0.23831 | 0.076011 | 615 | 0.29025 | 0.34249 | 395 | 0.18642 | 0.21997 | 184.4572 | 58.8349 | 628.9989 | 200.6269 | 2411.2562 | 8222.3838 | 0 | 0 | 0 | 0 | 8222.3838 | 8423.0107 | 10.4744 | 10.7299 | 785.8 | 8085.3114 | 10.2893 | 0
| 17:19:51 | 25.21 | 37.06 | 24.4 | 18.97 | 18.44 | 18.11 | 17.57 | 17.19 | 19.12 | 19.38 | 17.37 | 13.84 | 12.5 | 67.85 | 43.45 | 42.37 | 151.44 | 384.9 | 53.65 | 52.33 | 25.85 | 76.82 | 81.25 | 70.9 | 0 | 0 | 10.53 | 10.21 | 10.28 | 10.12 | -1 | -1 | -1 | -1 | 381.12 | 770 | 17:19:51 | 8.6167 | 770 | 0 | 0 | 0 | 18.2333 | 25.21 | 6.9767 | 10.2347 | 10.4816 | 10.1621 | 79.035 | 10.3312 | 0 | 0 | 0.18147 | 0.068319 | 615 | 0.29025 | 0.34249 | 395 | 0.18642 | 0.21997 | 140.4623 | 52.8808 | 478.9766 | 180.3237 | 2403.7911 | 8196.9275 | 0 | 0 | 0 | 0 | 8196.9275 | 8377.2512 | 10.6454 | 10.8795 | 782.8 | 8117.0339 | 10.3704 | 0
| 17:20:01 | 25.29 | 37.14 | 24.32 | 18.97 | 18.4 | 18.12 | 17.6 | 17.22 | 19.16 | 19.38 | 17.51 | 13.8 | 12.53 | 67.92 | 43.46 | 42.33 | 151.32 | 385.77 | 53.65 | 52.44 | 25.86 | 76.82 | 81.25 | 70.79 | 0 | 0 | 10.6 | 10.26 | 10.23 | 10.12 | -1 | -1 | -1 | -1 | 381.13 | 768 | 17:20:01 | 8.7833 | 768 | 0 | 0 | 0 | 18.245 | 25.29 | 7.045 | 10.185 | 10.555 | 10.2112 | 79.035 | 10.3389 | 0 | 0 | 0.24715 | 0.060621 | 615 | 0.29025 | 0.34249 | 395 | 0.18642 | 0.21997 | 191.2989 | 46.9229 | 652.3294 | 160.007 | 2427.3351 | 8277.2128 | 0 | 0 | 0 | 0 | 8277.2128 | 8437.2197 | 10.7776 | 10.986 | 779 | 8143.6651 | 10.4563 | 0
| 17:20:12 | 25.37 | 37.14 | 24.32 | 19.13 | 18.42 | 18.15 | 17.64 | 17.27 | 19.21 | 19.42 | 17.53 | 13.79 | 12.58 | 67.97 | 43.51 | 42.47 | 151.75 | 385.94 | 53.85 | 52.76 | 25.86 | 77.03 | 81.57 | 71.1 | 0 | 0 | 10.72 | 10.26 | 10.27 | 10.19 | -1 | -1 | -1 | -1 | 381.13 | 768 | 17:20:12 | 8.9667 | 768 | 0 | 0 | 0 | 18.3033 | 25.37 | 7.0667 | 10.2236 | 10.672 | 10.2112 | 79.3 | 10.4128 | 0 | 0 | 0.29023 | 0 | 615 | 0.29025 | 0.34249 | 395 | 0.18642 | 0.21997 | 224.6448 | 0 | 766.0389 | 0 | 2434.8003 | 8302.6691 | 0 | 0 | 0 | 0 | 8302.6691 | 8302.6691 | 10.8108 | 10.8108 | 775.4 | 8180.8705 | 10.5531 | 0
| 17:20:22 | 25.22 | 37.19 | 24.3 | 19.11 | 18.44 | 18.15 | 17.63 | 17.3 | 19.16 | 19.38 | 17.54 | 13.92 | 12.58 | 68 | 43.58 | 42.49 | 151.31 | 386.63 | 53.64 | 52.76 | 25.86 | 77.03 | 81.57 | 71.2 | 0 | 0 | 10.62 | 10.29 | 10.21 | 10.19 | -1 | -1 | -1 | -1 | 381.13 | 780 | 17:20:22 | 9.1333 | 780 | 0 | 0 | 0 | 18.2983 | 25.22 | 6.9217 | 10.1707 | 10.5756 | 10.2395 | 79.3 | 10.4095 | 0 | 0 | 0.19714 | 0 | 615 | 0.29025 | 0.34249 | 395 | 0.18642 | 0.21997 | 152.5952 | 0 | 520.3495 | 0 | 2384.841 | 8132.3077 | 0 | 0 | 0 | 0 | 8132.3077 | 8132.3077 | 10.426 | 10.426 | 774.2 | 8226.3002 | 10.6268 | 0
| 17:20:32 | 25.36 | 37.19 | 24.26 | 19.12 | 18.52 | 18.17 | 17.67 | 17.29 | 19.25 | 19.46 | 17.64 | 13.85 | 12.61 | 68.11 | 43.56 | 42.55 | 151.6 | 386.5 | 53.85 | 52.56 | 25.75 | 77.04 | 81.47 | 71.2 | 0 | 0 | 10.67 | 10.25 | 10.23 | 10.22 | -1 | -1 | -1 | -1 | 381.13 | 790 | 17:20:32 | 9.3 | 790 | 0 | 0 | 0 | 18.3367 | 25.36 | 7.0233 | 10.1863 | 10.6245 | 10.1952 | 79.255 | 10.429 | 0 | 0 | 0.2265 | 0 | 615 | 0.29025 | 0.34249 | 395 | 0.18642 | 0.21997 | 175.3216 | 0 | 597.8468 | 0 | 2419.8699 | 8251.7565 | 0 | 0 | 0 | 0 | 8251.7565 | 8251.7565 | 10.4453 | 10.4453 | 775.2 | 8232.1747 | 10.621 | 0
| 17:20:43 | 25.42 | 37.24 | 24.27 | 19.14 | 18.53 | 18.22 | 17.71 | 17.34 | 19.25 | 19.47 | 17.69 | 13.91 | 12.67 | 68.22 | 43.63 | 42.65 | 152.41 | 387.01 | 53.65 | 52.66 | 25.75 | 77.04 | 81.68 | 71.2 | 0 | 0 | 10.73 | 10.28 | 10.2 | 10.24 | -1 | -1 | -1 | -1 | 381.14 | 789 | 17:20:43 | 9.4833 | 789 | 0 | 0 | 0 | 18.365 | 25.42 | 7.055 | 10.154 | 10.6837 | 10.2234 | 79.36 | 10.4619 | 0 | 0 | 0.25281 | 0 | 615 | 0.29025 | 0.34249 | 395 | 0.18642 | 0.21997 | 195.6804 | 0 | 667.2703 | 0 | 2430.7806 | 8288.9618 | 0 | 0 | 0 | 0 | 8288.9618 | 8288.9618 | 10.5057 | 10.5057 | 779 | 8250.5816 | 10.5931 | 0
| 17:20:53 | 25.55 | 37.27 | 24.19 | 19.04 | 18.6 | 18.24 | 17.76 | 17.3 | 19.28 | 19.53 | 17.95 | 13.93 | 12.66 | 68.22 | 43.64 | 42.52 | 151.84 | 387.46 | 54.06 | 52.78 | 25.87 | 77.24 | 81.69 | 71.53 | 0 | 0 | 10.85 | 10.34 | 10.23 | 10.28 | -1 | -1 | -1 | -1 | 381.14 | 789 | 17:20:53 | 9.65 | 789 | 0 | 0 | 0 | 18.37 | 25.55 | 7.18 | 10.1831 | 10.7929 | 10.2889 | 79.465 | 10.4793 | 0 | 0 | 0.3446 | 0 | 615 | 0.29025 | 0.34249 | 395 | 0.18642 | 0.21997 | 266.7305 | 0 | 909.551 | 0 | 2473.849 | 8435.8251 | 0 | 0 | 0 | 0 | 8435.8251 | 8435.8251 | 10.6918 | 10.6918 | 783.2 | 8282.304 | 10.5759 | 0
| 17:21:04 | 25.31 | 37.28 | 24.34 | 19.18 | 18.53 | 18.24 | 17.68 | 17.28 | 19.21 | 19.49 | 18.1 | 13.91 | 12.62 | 68.26 | 43.68 | 42.57 | 151.92 | 387.58 | 54.27 | 52.88 | 25.87 | 77.06 | 81.68 | 71.41 | 0 | 0 | 10.7 | 10.35 | 10.36 | 10.25 | -1 | -1 | -1 | -1 | 381.14 | 789 | 17:21:04 | 9.8333 | 789 | 0 | 0 | 0 | 18.3533 | 25.31 | 6.9567 | 10.3172 | 10.658 | 10.2946 | 79.37 | 10.4555 | 0 | 0 | 0.23352 | 0 | 615 | 0.29025 | 0.34249 | 395 | 0.18642 | 0.21997 | 180.754 | 0 | 616.3711 | 0 | 2396.9001 | 8173.4294 | 0 | 0 | 0 | 0 | 8173.4294 | 8173.4294 | 10.3592 | 10.3592 | 787.4 | 8256.4561 | 10.4856 | 0
| 17:21:14 | 25.12 | 37.4 | 24.39 | 19.14 | 18.54 | 18.23 | 17.68 | 17.3 | 19.3 | 19.53 | 18.11 | 13.98 | 12.63 | 68.37 | 43.75 | 42.6 | 151.73 | 387.92 | 54.07 | 52.36 | 25.76 | 77.06 | 81.68 | 71.31 | 0 | 0 | 10.48 | 10.37 | 10.36 | 10.26 | -1 | -1 | -1 | -1 | 381.14 | 791 | 17:21:14 | 10 | 791 | 0 | 0 | 0 | 18.365 | 25.12 | 6.755 | 10.3099 | 10.4308 | 10.3183 | 79.37 | 10.4633 | 0 | 0 | 0 | 0 | 615 | 0.29025 | 0.34249 | 395 | 0.18642 | 0.21997 | 0 | 0 | 0 | 0 | 2327.4164 | 7936.49 | 0 | 0 | 0 | 0 | 7936.49 | 7936.49 | 10.0335 | 10.0335 | 789.6 | 8217.2926 | 10.4071 | 0
| 17:21:24 | 25.29 | 37.41 | 24.46 | 19.15 | 18.52 | 18.24 | 17.68 | 17.32 | 19.28 | 19.48 | 18.07 | 13.98 | 12.66 | 68.42 | 43.76 | 42.59 | 151.96 | 388.6 | 53.86 | 52.25 | 25.65 | 76.85 | 81.48 | 71.32 | 0 | 0 | 10.56 | 10.33 | 10.36 | 10.23 | -1 | -1 | -1 | -1 | 381.14 | 790 | 17:21:24 | 10.1667 | 790 | 0 | 0 | 0 | 18.365 | 25.29 | 6.925 | 10.313 | 10.5161 | 10.2792 | 79.165 | 10.4358 | 0 | 0 | 0.11136 | 0 | 615 | 0.29025 | 0.34249 | 395 | 0.18642 | 0.21997 | 86.1974 | 0 | 293.9331 | 0 | 2385.9895 | 8136.224 | 0 | 0 | 0 | 0 | 8136.224 | 8136.224 | 10.299 | 10.299 | 789.6 | 8194.1861 | 10.3778 | 0
| 17:21:35 | 25.49 | 37.39 | 24.26 | 19.32 | 18.55 | 18.25 | 17.73 | 17.42 | 19.35 | 19.51 | 18.02 | 14.01 | 12.68 | 68.52 | 43.73 | 42.68 | 151.85 | 387.95 | 53.86 | 52.47 | 25.65 | 77.04 | 81.59 | 71.12 | 0 | 0 | 10.74 | 10.32 | 10.24 | 10.28 | -1 | -1 | -1 | -1 | 381.15 | 789 | 17:21:35 | 10.35 | 789 | 0 | 0 | 0 | 18.4367 | 25.49 | 7.0533 | 10.1882 | 10.6896 | 10.2678 | 79.315 | 10.5038 | 0 | 0 | 0.21686 | 0 | 615 | 0.29025 | 0.34249 | 395 | 0.18642 | 0.21997 | 167.8531 | 0 | 572.379 | 0 | 2430.2063 | 8287.0036 | 0 | 0 | 0 | 0 | 8287.0036 | 8287.0036 | 10.5032 | 10.5032 | 789.6 | 8193.7944 | 10.3773 | 0
| 17:21:45 | 25.44 | 37.36 | 24.3 | 19.27 | 18.59 | 18.25 | 17.8 | 17.41 | 19.36 | 19.58 | 18.02 | 13.96 | 12.73 | 68.51 | 43.78 | 42.62 | 151.79 | 388.33 | 53.65 | 52.36 | 25.53 | 77.07 | 81.69 | 71.23 | 0 | 0 | 10.68 | 10.26 | 10.22 | 10.31 | -1 | -1 | -1 | -1 | 381.15 | 772 | 17:21:45 | 10.5167 | 772 | 0 | 0 | 0 | 18.4467 | 25.44 | 6.9933 | 10.1726 | 10.6346 | 10.2021 | 79.38 | 10.5192 | 0 | 0 | 0.14643 | 0 | 615 | 0.29025 | 0.34249 | 395 | 0.18642 | 0.21997 | 113.3387 | 0 | 386.485 | 0 | 2409.5335 | 8216.5093 | 0 | 0 | 0 | 0 | 8216.5093 | 8216.5093 | 10.6431 | 10.6431 | 786.2 | 8149.9313 | 10.3676 | 0
| 17:21:55 | 25.21 | 37.36 | 24.53 | 19.26 | 18.54 | 18.23 | 17.72 | 17.33 | 19.34 | 19.55 | 17.85 | 13.95 | 12.7 | 68.58 | 43.77 | 42.69 | 152.22 | 388.57 | 54.07 | 52.57 | 25.77 | 77.25 | 81.79 | 71.22 | 0 | 0 | 10.58 | 10.35 | 10.45 | 10.29 | -1 | -1 | -1 | -1 | 381.15 | 773 | 17:21:55 | 10.6833 | 773 | 0 | 0 | 0 | 18.4033 | 25.21 | 6.8067 | 10.3981 | 10.5305 | 10.2996 | 79.52 | 10.509 | 0 | 0 | 0.052512 | 0 | 615 | 0.29025 | 0.34249 | 395 | 0.18642 | 0.21997 | 40.6462 | 0 | 138.6036 | 0 | 2345.218 | 7997.1935 | 0 | 0 | 0 | 0 | 7997.1935 | 7997.1935 | 10.3457 | 10.3457 | 783 | 8114.6841 | 10.3649 | 0
| 17:22:06 | 25.27 | 37.42 | 24.61 | 19.26 | 18.58 | 18.29 | 17.82 | 17.39 | 19.34 | 19.63 | 17.81 | 14.03 | 12.71 | 68.64 | 43.81 | 42.7 | 152.1 | 388.86 | 54.07 | 52.57 | 25.77 | 77.25 | 81.79 | 71.22 | 0 | 0 | 10.62 | 10.39 | 10.5 | 10.32 | -1 | -1 | -1 | -1 | 381.15 | 792 | 17:22:06 | 10.8667 | 792 | 0 | 0 | 0 | 18.4467 | 25.27 | 6.8233 | 10.4488 | 10.5688 | 10.3338 | 79.52 | 10.5381 | 0 | 0 | 0.061739 | 0 | 615 | 0.29025 | 0.34249 | 395 | 0.18642 | 0.21997 | 47.7878 | 0 | 162.9564 | 0 | 2350.9605 | 8016.7753 | 0 | 0 | 0 | 0 | 8016.7753 | 8016.7753 | 10.1222 | 10.1222 | 783.2 | 8130.7411 | 10.3826 | 0
| 17:22:17 | 25.33 | 37.4 | 24.46 | 19.18 | 18.59 | 18.24 | 17.69 | 17.32 | 19.35 | 19.62 | 17.77 | 14.06 | 12.71 | 68.71 | 43.78 | 42.68 | 152.06 | 389.25 | 54.3 | 52.99 | 25.77 | 77.25 | 81.69 | 71.44 | 0 | 0 | 10.74 | 10.37 | 10.45 | 10.3 | -1 | -1 | -1 | -1 | 381.15 | 793 | 17:22:17 | 11.05 | 793 | 0 | 0 | 0 | 18.395 | 25.33 | 6.935 | 10.3987 | 10.6935 | 10.3224 | 79.47 | 10.4967 | 0 | 0 | 0.22775 | 0 | 615 | 0.29025 | 0.34249 | 395 | 0.18642 | 0.21997 | 176.284 | 0 | 601.1283 | 0 | 2389.4349 | 8147.9731 | 0 | 0 | 0 | 0 | 8147.9731 | 8147.9731 | 10.2749 | 10.2749 | 783.8 | 8133.091 | 10.3778 | 0
| 17:22:27 | 25.18 | 37.51 | 24.54 | 19.2 | 18.6 | 18.31 | 17.71 | 17.3 | 19.28 | 19.62 | 17.89 | 14.05 | 12.7 | 68.8 | 43.91 | 42.84 | 152.44 | 389.53 | 54.3 | 52.78 | 25.78 | 77.27 | 81.69 | 71.34 | 0 | 0 | 10.6 | 10.44 | 10.5 | 10.3 | -1 | -1 | -1 | -1 | 381.16 | 794 | 17:22:27 | 11.2167 | 794 | 0 | 0 | 0 | 18.4 | 25.18 | 6.78 | 10.4494 | 10.5541 | 10.3894 | 79.48 | 10.5014 | 0 | 0 | 0.083717 | 0 | 615 | 0.29025 | 0.34249 | 395 | 0.18642 | 0.21997 | 64.7994 | 0 | 220.9661 | 0 | 2336.0301 | 7965.8627 | 0 | 0 | 0 | 0 | 7965.8627 | 7965.8627 | 10.0326 | 10.0326 | 784.8 | 8068.8628 | 10.2837 | 0
| 17:22:38 | 25.48 | 37.47 | 24.47 | 19.32 | 18.6 | 18.3 | 17.71 | 17.37 | 19.39 | 19.64 | 17.82 | 14.12 | 12.75 | 68.85 | 43.9 | 42.79 | 152.75 | 390.09 | 53.88 | 52.68 | 25.56 | 77.17 | 81.69 | 71.24 | 0 | 0 | 10.77 | 10.33 | 10.37 | 10.32 | -1 | -1 | -1 | -1 | 381.16 | 794 | 17:22:38 | 11.4 | 794 | 0 | 0 | 0 | 18.4483 | 25.48 | 7.0317 | 10.3232 | 10.7266 | 10.2765 | 79.43 | 10.5271 | 0 | 0 | 0.23058 | 0 | 615 | 0.29025 | 0.34249 | 395 | 0.18642 | 0.21997 | 178.4756 | 0 | 608.6019 | 0 | 2422.7412 | 8261.5473 | 0 | 0 | 0 | 0 | 8261.5473 | 8261.5473 | 10.405 | 10.405 | 789.2 | 8077.8704 | 10.2361 | 0
| 17:22:48 | 25.3 | 37.59 | 24.43 | 19.25 | 18.57 | 18.31 | 17.78 | 17.41 | 19.34 | 19.58 | 17.7 | 14.04 | 12.74 | 68.87 | 43.98 | 42.87 | 152.56 | 390.73 | 53.88 | 52.77 | 25.56 | 77.06 | 81.79 | 71.04 | 0 | 0 | 10.68 | 10.39 | 10.34 | 10.3 | -1 | -1 | -1 | -1 | 381.16 | 794 | 17:22:48 | 11.5667 | 794 | 0 | 0 | 0 | 18.4433 | 25.3 | 6.8567 | 10.2981 | 10.629 | 10.3448 | 79.425 | 10.5231 | 0 | 0 | 0.13695 | 0 | 615 | 0.29025 | 0.34249 | 395 | 0.18642 | 0.21997 | 106.0013 | 0 | 361.4645 | 0 | 2362.4454 | 8055.9388 | 0 | 0 | 0 | 0 | 8055.9388 | 8055.9388 | 10.146 | 10.146 | 793.4 | 8089.6194 | 10.1961 | 0
| 17:22:58 | 25.45 | 37.51 | 24.45 | 19.27 | 18.65 | 18.35 | 17.83 | 17.4 | 19.37 | 19.61 | 17.58 | 14.11 | 12.8 | 68.94 | 43.95 | 42.88 | 151.77 | 390.45 | 54.1 | 52.78 | 25.56 | 77.27 | 82.01 | 71.34 | 0 | 0 | 10.78 | 10.35 | 10.4 | 10.35 | -1 | -1 | -1 | -1 | 381.16 | 793 | 17:22:58 | 11.7333 | 793 | 0 | 0 | 0 | 18.4783 | 25.45 | 6.9717 | 10.3535 | 10.7279 | 10.2992 | 79.64 | 10.5756 | 0 | 0 | 0.18332 | 0 | 615 | 0.29025 | 0.34249 | 395 | 0.18642 | 0.21997 | 141.8923 | 0 | 483.8526 | 0 | 2402.0683 | 8191.053 | 0 | 0 | 0 | 0 | 8191.053 | 8191.053 | 10.3292 | 10.3292 | 793.6 | 8124.475 | 10.2375 | 0
| 17:23:09 | 25.46 | 37.57 | 24.48 | 19.36 | 18.54 | 18.3 | 17.81 | 17.47 | 19.46 | 19.62 | 17.78 | 14.02 | 12.72 | 68.96 | 43.94 | 42.8 | 152.61 | 389.88 | 54.09 | 52.99 | 25.56 | 77.27 | 81.81 | 71.44 | 0 | 0 | 10.82 | 10.38 | 10.42 | 10.36 | -1 | -1 | -1 | -1 | 381.17 | 793 | 17:23:09 | 11.9167 | 793 | 0 | 0 | 0 | 18.49 | 25.46 | 6.97 | 10.3704 | 10.7778 | 10.3334 | 79.54 | 10.57 | 0 | 0 | 0.2389 | 0 | 615 | 0.29025 | 0.34249 | 395 | 0.18642 | 0.21997 | 184.915 | 0 | 630.5601 | 0 | 2401.4941 | 8189.0948 | 0 | 0 | 0 | 0 | 8189.0948 | 8189.0948 | 10.3267 | 10.3267 | 793.6 | 8132.6993 | 10.2479 | 0
| 17:23:19 | 25.26 | 37.61 | 24.4 | 19.24 | 18.6 | 18.34 | 17.79 | 17.4 | 19.4 | 19.64 | 17.86 | 14.05 | 12.75 | 69.02 | 43.98 | 42.89 | 151.85 | 390.73 | 53.88 | 52.89 | 25.56 | 77.27 | 81.7 | 71.25 | 0 | 0 | 10.68 | 10.41 | 10.33 | 10.33 | -1 | -1 | -1 | -1 | 381.17 | 794 | 17:23:19 | 12.0833 | 794 | 0 | 0 | 0 | 18.4617 | 25.26 | 6.7983 | 10.2793 | 10.6278 | 10.3562 | 79.485 | 10.5435 | 0 | 0 | 0.11538 | 0 | 615 | 0.29025 | 0.34249 | 395 | 0.18642 | 0.21997 | 89.3067 | 0 | 304.5359 | 0 | 2342.3468 | 7987.4026 | 0 | 0 | 0 | 0 | 7987.4026 | 7987.4026 | 10.0597 | 10.0597 | 793.6 | 8137.0073 | 10.2533 | 0
| 17:23:30 | 25.48 | 37.65 | 24.56 | 19.31 | 18.7 | 18.4 | 17.86 | 17.44 | 19.45 | 19.65 | 17.73 | 14.08 | 12.79 | 69.05 | 44.04 | 42.92 | 152.15 | 390.81 | 53.9 | 52.47 | 25.57 | 77.28 | 81.82 | 71.25 | 0 | 0 | 10.73 | 10.44 | 10.43 | 10.37 | -1 | -1 | -1 | -1 | 381.17 | 776 | 17:23:30 | 12.2667 | 776 | 0 | 0 | 0 | 18.5267 | 25.48 | 6.9533 | 10.3838 | 10.6832 | 10.3832 | 79.55 | 10.596 | 0 | 0 | 0.11814 | 0 | 615 | 0.29025 | 0.34249 | 395 | 0.18642 | 0.21997 | 91.4426 | 0 | 311.8192 | 0 | 2395.7516 | 8169.513 | 0 | 0 | 0 | 0 | 8169.513 | 8169.513 | 10.5277 | 10.5277 | 790 | 8118.6004 | 10.2779 | 0
end test | 17:23:40 | 25.41 | 37.59 | 24.52 | 19.36 | 18.58 | 18.35 | 17.79 | 17.42 | 19.46 | 19.67 | 17.83 | 14.05 | 12.74 | 69.16 | 44 | 42.93 | 152.38 | 390.62 | 53.69 | 52.57 | 25.46 | 77.07 | 81.7 | 71.25 | 0 | 0 | 10.71 | 10.35 | 10.36 | 10.34 | -1 | -1 | -1 | -1 | 381.17 | 776 | 17:23:40 | 12.4333 | 776 | 0 | 0 | 0 | 18.4933 | 25.41 | 6.9167 | 10.3175 | 10.6587 | 10.3037 | 79.385 | 10.5513 | 0 | 0 | 0.13845 | 0 | 615 | 0.29025 | 0.34249 | 395 | 0.18642 | 0.21997 | 107.1666 | 0 | 365.438 | 0 | 2383.1182 | 8126.4332 | 0 | 0 | 0 | 0 | 8126.4332 | 8126.4332 | 10.4722 | 10.4722 | 786.4 | 8132.6993 | 10.3431 | 0
-43.2
-43.0167
-42.85
-42.6833
-42.5167
-42.3333
-42.1667
-41.9833
-41.8
-41.6167
-41.45
-41.2833
-41.1167
-40.9333
-40.7667
-40.6
-40.4333
-40.25
-40.05
-39.85
-39.6833
-39.5
-39.3333
-39.15
-38.9667
-38.8
-38.6333
-38.45
-38.2667
-38.1
-37.9167
-37.7333
-37.5667
-37.3833
-37.2
-37.0333
-36.8667
-36.7
-36.5167
-36.3
-36.1333
-35.95
-35.7833
-35.6167
-35.4333
-35.25
-35.0833
-34.9167
-34.75
-34.5667
-34.4
-34.2333
-34.05
-33.8833
-33.7
-33.5333
-33.3667
-33.1833
-33.0167
-32.8333
-32.65
-32.4667
-32.3
-32.1333
-31.95
-31.7833
-31.6
-31.4333
-31.2667
-31.1
-30.9167
-30.7333
-30.5667
-30.4
-30.2333
-30.0667
-29.8833
-29.7
-29.5333
-29.3667
-29.1833
-29.0167
-28.8333
-28.6667
-28.4833
-28.3167
-28.1333
-27.9667
-27.7833
-27.5833
-27.4
-27.2167
-27.05
-26.8667
-26.6833
-26.4833
-26.3167
-26.1333
-25.95
-25.7833
-25.6167
-25.4333
-25.25
-25.0667
-24.9
-24.7167
-24.55
-24.3667
-24.1833
-24.0167
-23.8
-23.6167
-23.45
-23.2667
-23.0833
-22.9167
-22.75
-22.5667
-22.4
-22.2167
-22.0333
-21.8333
-21.6333
-21.4333
-21.2667
-21.1
-20.9167
-20.7333
-20.5333
-20.35
-20.1833
-20.0167
-19.8333
-19.6667
-19.4833
-19.3167
-19.1333
-18.95
-18.7833
-18.6167
-18.4333
-18.2667
-18.0833
-17.9167
-17.75
-17.5667
-17.4
-17.2333
-17.0667
-16.8833
-16.7
-16.5333
-16.35
-16.1667
-16
-15.8167
-15.6333
-15.4333
-15.25
-15.0667
-14.8833
-14.7
-14.5167
-14.35
-14.1833
-14
-13.8333
-13.6667
-13.4833
-13.3167
-13.1333
-12.9667
-12.8
-12.6333
-12.4333
-12.2667
-12.1
-11.9167
-11.75
-11.55
-11.3833
-11.2
-11.0333
-10.8667
-10.6833
-10.5167
-10.3333
-10.1667
-10
-9.8167
-9.6167
-9.4333
-9.2667
-9.1
-8.9167
-8.75
-8.5833
-8.4
-8.2
-8.0333
-7.8333
-7.6667
-7.4833
-7.3167
-7.1333
-6.9667
-6.8
-6.6167
-6.4333
-6.2667
-6.1
-5.9333
-5.75
-5.5833
-5.4167
-5.25
-5.0833
-4.9
-4.7333
-4.5667
-4.3833
-4.2167
-4.0333
-3.8667
-3.7
-3.5167
-3.3
-3.1333
-2.95
-2.7833
-2.6
-2.4167
-2.25
-2.0833
-1.9167
-1.7333
-1.55
-1.3833
-1.2167
-1.05
-0.86667
-0.7
-0.51667
-0.33333
-0.16667