## Sheet1
0 | 1 | AT1 | AT2 | AT3 | AT4 | AT5 | AT6 | AT7 | AT8 | AT9 | AT10 | LT1 | LT2 | LT3 | LT4 | LT5 | LT6 | P1 | P2 | RH1 | RH2 | RH3 | RH4 | RH5 | RH6 | RH7 | RH8 | W1 | W2 | W3 | W4 | W5 | W6 | W7 | W8 | 36 | 37 | valid_times | TimeDifference | Total_Power | U_Config | Super_Heat | Sub_Cool | T_supply | T_return | dT[C] | W_U_Inlet | W_S_Inlet | W_exhaust | RH_avg | W_supply | Exhaust Humidity Delta (Standard) | Exhaust Humidity Delta (Averaged Inlet) | Supply Humidity Delta (Standard) [g/kg] | Supply Humidity Delta (Averaged Inlet) | Process_airflow | Process V_dot | Process M_dot [kg/s] | Regen Airflow | Regen V_dot | Regen M_dot [kg/s] | Q_lat_Supply [W] | Q_lat_Supply Filtered[W] | Q_lat_Supply [BTU/hr] | Q_lat_Supply Filtered[BTU/hr] | Q_sens [W] | Q_sens [BTU/hr] | Q_lat_Exhaust [W] | Q_lat_Exhaust Filtered[W] | Q_lat_Exhaust [BTU/hr] | Q_lat_Exhaust Filtered[BTU/hr] | Q_tot (Exhaust Latent) [BTU/hr] | Q_tot (Supply Latent) [BTU/hr] | EER (Exhaust Latent) [BTU/Wh] | EER (Supply Latent) [BTU/Wh] | Average_Power_5min | Average_Q_tot_5min | EER_5min | Q_lat_5min
| 17:11:14 | 24.65 | 34.41 | 23.8 | 19.18 | 17.97 | 17.72 | 17.3 | 17.16 | 19.13 | 19.58 | 18.52 | 13.41 | 11.98 | 64.27 | 40.72 | 39.32 | 148.56 | 359.74 | 54.99 | 53.1 | 32.57 | 74.82 | 79.62 | 66.85 | 0 | 0 | 10.33 | 11.14 | 10.16 | 9.71 | -1 | -1 | -1 | -1 | 381.02 | 744 | 17:11:14 | 0 | 744 | 0 | 0 | 0 | 18.0767 | 24.65 | 6.5733 | 10.1174 | 10.2832 | 11.0831 | 77.22 | 9.9897 | 0.79987 | 0.65236 | 0.29359 | 0.44109 | 615 | 0.29025 | 0.34249 | 395 | 0.18642 | 0.21997 | 227.2457 | 341.418 | 774.9078 | 1164.2355 | 2264.8237 | 7723.0488 | 397.6472 | 324.317 | 1355.9771 | 1105.921 | 9079.0258 | 8887.2843 | 12.203 | 11.9453 | 728 | 9860.8733 | 13.5551 | 2386.513
| 17:11:25 | 24.68 | 34.47 | 23.94 | 18.99 | 18.11 | 17.7 | 17.35 | 17.17 | 19.12 | 19.53 | 18.61 | 13.46 | 12 | 64.41 | 40.77 | 39.42 | 148.92 | 360.24 | 54.79 | 52.89 | 32.02 | 75.11 | 79.61 | 67.13 | 0 | 0 | 10.31 | 10.98 | 10.21 | 9.73 | -1 | -1 | -1 | -1 | 381.02 | 746 | 17:11:25 | 0.18333 | 746 | 0 | 0 | 0 | 18.0733 | 24.68 | 6.6067 | 10.1666 | 10.2606 | 10.9297 | 77.36 | 10.0059 | 0.66908 | 0.49892 | 0.25466 | 0.42482 | 615 | 0.29025 | 0.34249 | 395 | 0.18642 | 0.21997 | 197.1156 | 328.8233 | 672.1642 | 1121.2873 | 2276.3086 | 7762.2123 | 332.629 | 248.0363 | 1134.2648 | 845.8036 | 8896.4771 | 8883.4996 | 11.9256 | 11.9082 | 730.8 | 9581.9005 | 13.1284 | 1961.0686
| 17:11:37 | 24.57 | 34.58 | 23.86 | 19.01 | 18.03 | 17.66 | 17.29 | 17.17 | 19.27 | 19.52 | 18.57 | 13.29 | 11.93 | 64.57 | 40.81 | 39.36 | 148.1 | 360.45 | 54.57 | 52.68 | 31.8 | 75.01 | 79.81 | 67.43 | 0 | 0 | 10.2 | 10.97 | 10.12 | 9.74 | -1 | -1 | -1 | -1 | 381.02 | 746 | 17:11:37 | 0.38333 | 746 | 0 | 0 | 0 | 18.0717 | 24.57 | 6.4983 | 10.0757 | 10.1511 | 10.9209 | 77.41 | 10.0114 | 0.7698 | 0.49015 | 0.13967 | 0.41931 | 615 | 0.29025 | 0.34249 | 395 | 0.18642 | 0.21997 | 108.1082 | 324.5621 | 368.649 | 1106.7567 | 2238.9826 | 7634.9308 | 382.6982 | 243.6749 | 1305.0008 | 830.9316 | 8939.9316 | 8741.6875 | 11.9838 | 11.7181 | 736.4 | 9321.6502 | 12.6725 | 1648.7308
| 17:11:47 | 24.56 | 34.69 | 23.84 | 18.84 | 17.94 | 17.71 | 17.24 | 17.04 | 19.11 | 19.44 | 18.47 | 13.3 | 11.87 | 64.67 | 40.9 | 39.43 | 148.47 | 361.19 | 53.96 | 52.25 | 30.91 | 74.99 | 79.6 | 67.71 | 0 | 0 | 10.11 | 10.73 | 9.99 | 9.69 | -1 | -1 | -1 | -1 | 381.02 | 747 | 17:11:47 | 0.55 | 747 | 0 | 0 | 0 | 17.98 | 24.56 | 6.58 | 9.9491 | 10.0608 | 10.6761 | 77.295 | 9.9379 | 0.61529 | 0.24533 | 0.12285 | 0.49281 | 615 | 0.29025 | 0.34249 | 395 | 0.18642 | 0.21997 | 95.0924 | 381.454 | 324.2652 | 1300.7582 | 2267.1207 | 7730.8815 | 305.8853 | 121.962 | 1043.069 | 415.8905 | 8773.9504 | 9031.6397 | 11.7456 | 12.0905 | 742 | 8956.3904 | 12.073 | 1256.8397
| 17:11:57 | 24.62 | 34.73 | 23.81 | 18.88 | 17.89 | 17.66 | 17.18 | 17 | 19.03 | 19.31 | 18.36 | 13.27 | 11.87 | 64.75 | 40.96 | 39.64 | 148.26 | 361.17 | 53.76 | 52.05 | 30.7 | 75.07 | 79.57 | 67.59 | 0 | 0 | 10.1 | 10.68 | 9.94 | 9.65 | -1 | -1 | -1 | -1 | 381.02 | 746 | 17:11:57 | 0.71667 | 746 | 0 | 0 | 0 | 17.94 | 24.62 | 6.68 | 9.8935 | 10.0583 | 10.6262 | 77.32 | 9.9158 | 0.56798 | 0.19549 | 0.14245 | 0.51494 | 615 | 0.29025 | 0.34249 | 395 | 0.18642 | 0.21997 | 110.2638 | 398.5801 | 375.9997 | 1359.1582 | 2301.5754 | 7848.3721 | 282.3659 | 97.1871 | 962.8677 | 331.4081 | 8811.2397 | 9207.5303 | 11.8113 | 12.3425 | 745.8 | 8900.1249 | 11.9339 | 1160.2359
| 17:12:07 | 24.69 | 34.82 | 23.89 | 18.81 | 17.9 | 17.67 | 17.2 | 16.97 | 18.92 | 19.3 | 18.19 | 13.29 | 11.92 | 64.88 | 41.08 | 39.61 | 148.44 | 362.53 | 53.96 | 52.37 | 30.48 | 75.57 | 79.88 | 68.09 | 0 | 0 | 10.21 | 10.65 | 10.02 | 9.7 | -1 | -1 | -1 | -1 | 381.02 | 748 | 17:12:07 | 0.88333 | 748 | 0 | 0 | 0 | 17.9117 | 24.69 | 6.7783 | 9.9796 | 10.1642 | 10.6024 | 77.725 | 9.9505 | 0.43819 | 0.17168 | 0.2137 | 0.48022 | 615 | 0.29025 | 0.34249 | 395 | 0.18642 | 0.21997 | 165.4129 | 371.7029 | 564.0578 | 1267.5069 | 2335.4559 | 7963.9045 | 217.8435 | 85.3483 | 742.8464 | 291.0377 | 8706.7509 | 9231.4114 | 11.64 | 12.3415 | 746.6 | 8825.6699 | 11.8213 | 1037.6097
| 17:12:18 | 24.45 | 34.85 | 23.68 | 18.86 | 17.91 | 17.67 | 17.22 | 16.92 | 18.93 | 19.25 | 17.9 | 13.39 | 11.98 | 64.99 | 41.14 | 39.75 | 149.21 | 362.52 | 53.96 | 52.48 | 30.27 | 75.76 | 80.18 | 68.36 | 0 | 0 | 10.09 | 10.6 | 9.89 | 9.73 | -1 | -1 | -1 | -1 | 381.03 | 729 | 17:12:18 | 1.0667 | 729 | 0 | 0 | 0 | 17.9183 | 24.45 | 6.5317 | 9.8523 | 10.0384 | 10.5459 | 77.97 | 9.9867 | 0.50752 | 0.11519 | 0.051764 | 0.44409 | 615 | 0.29025 | 0.34249 | 395 | 0.18642 | 0.21997 | 40.0668 | 343.7398 | 136.6276 | 1172.1527 | 2250.4676 | 7674.0943 | 252.3101 | 57.268 | 860.3773 | 195.284 | 8534.4716 | 8846.247 | 11.7071 | 12.1348 | 743.2 | 8753.2689 | 11.7776 | 982.8322
| 17:12:28 | 24.81 | 34.96 | 23.92 | 18.81 | 17.93 | 17.72 | 17.24 | 16.99 | 18.93 | 19.26 | 17.82 | 13.33 | 11.99 | 65.13 | 41.23 | 39.87 | 148.92 | 364.25 | 53.76 | 52.28 | 30.05 | 75.96 | 80.18 | 68.77 | 0 | 0 | 10.26 | 10.58 | 10 | 9.77 | -1 | -1 | -1 | -1 | 381.03 | 730 | 17:12:28 | 1.2333 | 730 | 0 | 0 | 0 | 17.9367 | 24.81 | 6.8733 | 9.9602 | 10.2207 | 10.533 | 78.07 | 10.0114 | 0.31235 | 0.10227 | 0.20926 | 0.41934 | 615 | 0.29025 | 0.34249 | 395 | 0.18642 | 0.21997 | 161.9748 | 324.585 | 552.334 | 1106.8349 | 2368.1878 | 8075.5206 | 155.2811 | 50.8404 | 529.5087 | 173.3658 | 8605.0293 | 9182.3555 | 11.7877 | 12.5786 | 740 | 8686.2884 | 11.7383 | 827.7338
| 17:12:38 | 24.68 | 34.95 | 23.56 | 18.75 | 17.9 | 17.68 | 17.19 | 16.92 | 18.9 | 19.17 | 17.62 | 13.42 | 12.01 | 65.18 | 41.28 | 39.99 | 148.37 | 364.35 | 54.38 | 52.89 | 29.94 | 76.15 | 80.49 | 69.06 | 0 | 0 | 10.31 | 10.54 | 9.9 | 9.77 | -1 | -1 | -1 | -1 | 381.03 | 732 | 17:12:38 | 1.4 | 732 | 0 | 0 | 0 | 17.89 | 24.68 | 6.79 | 9.8575 | 10.2606 | 10.4879 | 78.32 | 10.014 | 0.22731 | 0.057156 | 0.24655 | 0.4167 | 615 | 0.29025 | 0.34249 | 395 | 0.18642 | 0.21997 | 190.8356 | 322.5432 | 650.7493 | 1099.8723 | 2339.4756 | 7977.6117 | 113.0073 | 28.4146 | 385.3548 | 96.8937 | 8362.9666 | 9077.484 | 11.4248 | 12.4009 | 737 | 8604.0916 | 11.6742 | 696.191
| 17:12:49 | 24.88 | 35.01 | 23.65 | 18.81 | 17.95 | 17.75 | 17.26 | 16.96 | 18.9 | 19.17 | 17.65 | 13.45 | 12.06 | 65.23 | 41.33 | 40.04 | 149.34 | 364.71 | 54.07 | 52.37 | 29.61 | 76.34 | 80.59 | 69.25 | 0 | 0 | 10.33 | 10.45 | 9.9 | 9.82 | -1 | -1 | -1 | -1 | 381.04 | 740 | 17:12:49 | 1.5833 | 740 | 0 | 0 | 0 | 17.9383 | 24.88 | 6.9417 | 9.8546 | 10.2821 | 10.4054 | 78.465 | 10.0639 | 0.12331 | -0.025317 | 0.21817 | 0.3668 | 615 | 0.29025 | 0.34249 | 395 | 0.18642 | 0.21997 | 168.8738 | 283.913 | 575.8595 | 968.1433 | 2391.7319 | 8155.8058 | 61.3009 | -12.5861 | 209.0362 | -42.9184 | 8364.842 | 9123.9491 | 11.3038 | 12.3297 | 735.8 | 8514.8121 | 11.5727 | 545.4247
| 17:12:59 | 24.66 | 35.15 | 23.77 | 18.74 | 17.94 | 17.71 | 17.28 | 16.98 | 18.88 | 19.12 | 17.53 | 13.29 | 12.02 | 65.36 | 41.45 | 40.12 | 149.15 | 366.62 | 54.38 | 52.47 | 29.61 | 76.56 | 80.59 | 69.56 | 0 | 0 | 10.21 | 10.54 | 10.03 | 9.83 | -1 | -1 | -1 | -1 | 381.04 | 756 | 17:12:59 | 1.75 | 756 | 0 | 0 | 0 | 17.9217 | 24.66 | 6.7383 | 9.985 | 10.1654 | 10.4876 | 78.575 | 10.0675 | 0.32221 | 0.056882 | 0.097871 | 0.3632 | 615 | 0.29025 | 0.34249 | 395 | 0.18642 | 0.21997 | 75.7555 | 281.1275 | 258.3264 | 958.6449 | 2321.674 | 7916.9083 | 160.184 | 28.2784 | 546.2275 | 96.4294 | 8463.1358 | 8875.5532 | 11.1946 | 11.7401 | 737.4 | 8466.089 | 11.4836 | 506.1009
| 17:13:09 | 24.79 | 35.17 | 23.88 | 18.79 | 17.97 | 17.74 | 17.25 | 16.96 | 18.89 | 19.13 | 17.52 | 13.47 | 12.04 | 65.45 | 41.54 | 40.15 | 149.25 | 367.32 | 54.38 | 52.69 | 29.4 | 76.46 | 80.59 | 69.75 | 0 | 0 | 10.34 | 10.48 | 10.1 | 9.84 | -1 | -1 | -1 | -1 | 381.04 | 758 | 17:13:09 | 1.9167 | 758 | 0 | 0 | 0 | 17.9333 | 24.79 | 6.8567 | 10.0524 | 10.2896 | 10.4237 | 78.525 | 10.0685 | 0.13406 | -0.0070406 | 0.2211 | 0.3622 | 615 | 0.29025 | 0.34249 | 395 | 0.18642 | 0.21997 | 171.1384 | 280.3527 | 583.5821 | 956.0026 | 2362.4454 | 8055.9388 | 66.6455 | -3.5002 | 227.2613 | -11.9356 | 8283.2001 | 9011.9414 | 10.9277 | 11.8891 | 743.2 | 8415.8347 | 11.3277 | 379.4777
| 17:13:20 | 24.74 | 35.42 | 23.69 | 18.74 | 17.98 | 17.73 | 17.24 | 16.95 | 18.89 | 19.06 | 17.59 | 13.35 | 12.08 | 65.54 | 41.72 | 40.36 | 148.79 | 368.96 | 54.17 | 52.69 | 29.18 | 76.56 | 80.58 | 69.74 | 0 | 0 | 10.31 | 10.54 | 9.94 | 9.83 | -1 | -1 | -1 | -1 | 381.04 | 760 | 17:13:20 | 2.1 | 760 | 0 | 0 | 0 | 17.9217 | 24.74 | 6.8183 | 9.8973 | 10.2585 | 10.4905 | 78.57 | 10.0669 | 0.23208 | 0.059796 | 0.19157 | 0.36385 | 615 | 0.29025 | 0.34249 | 395 | 0.18642 | 0.21997 | 148.2785 | 281.6314 | 505.6295 | 960.3632 | 2349.2378 | 8010.9007 | 115.3767 | 29.7272 | 393.4345 | 101.3697 | 8404.3352 | 8971.2639 | 11.0583 | 11.8043 | 749.2 | 8375.6959 | 11.1819 | 352.2629
| 17:13:30 | 24.67 | 35.41 | 23.7 | 18.69 | 18.03 | 17.76 | 17.26 | 16.98 | 18.83 | 19.06 | 17.53 | 13.45 | 12.11 | 65.66 | 41.73 | 40.57 | 149.46 | 369.17 | 54.39 | 52.49 | 28.96 | 76.46 | 80.78 | 69.84 | 0 | 0 | 10.22 | 10.45 | 9.99 | 9.84 | -1 | -1 | -1 | -1 | 381.04 | 760 | 17:13:30 | 2.2667 | 760 | 0 | 0 | 0 | 17.925 | 24.67 | 6.745 | 9.9442 | 10.1755 | 10.4043 | 78.62 | 10.0756 | 0.22876 | -0.026455 | 0.099981 | 0.35519 | 615 | 0.29025 | 0.34249 | 395 | 0.18642 | 0.21997 | 77.3888 | 274.9297 | 263.8957 | 937.5102 | 2323.971 | 7924.741 | 113.7241 | -13.1518 | 387.7992 | -44.8475 | 8312.5401 | 8862.2511 | 10.9376 | 11.6609 | 754.8 | 8365.6106 | 11.0844 | 352.7517
| 17:13:42 | 24.76 | 35.46 | 23.93 | 18.69 | 18 | 17.79 | 17.33 | 16.99 | 18.85 | 19.07 | 17.23 | 13.44 | 12.13 | 65.79 | 41.82 | 40.57 | 149.71 | 369.18 | 54.4 | 52.49 | 28.97 | 76.56 | 80.79 | 69.94 | 0 | 0 | 10.28 | 10.49 | 10.13 | 9.86 | -1 | -1 | -1 | -1 | 381.04 | 741 | 17:13:42 | 2.4667 | 741 | 0 | 0 | 0 | 17.9417 | 24.76 | 6.8183 | 10.0869 | 10.2313 | 10.4372 | 78.675 | 10.0935 | 0.20586 | 0.0064097 | 0.13783 | 0.33727 | 615 | 0.29025 | 0.34249 | 395 | 0.18642 | 0.21997 | 106.6825 | 261.0609 | 363.7874 | 890.2176 | 2349.2378 | 8010.9007 | 102.3401 | 3.1865 | 348.9798 | 10.8661 | 8359.8805 | 8901.1183 | 11.2819 | 12.0123 | 755 | 8364.6183 | 11.08 | 380.7404
| 17:13:53 | 24.7 | 35.52 | 23.76 | 18.65 | 18.05 | 17.82 | 17.33 | 17.01 | 18.88 | 19.05 | 17.03 | 13.48 | 12.13 | 65.87 | 41.84 | 40.58 | 149.11 | 370.39 | 54.39 | 52.49 | 28.53 | 76.56 | 80.79 | 70.25 | 0 | 0 | 10.24 | 10.36 | 10.03 | 9.88 | -1 | -1 | -1 | -1 | 381.05 | 742 | 17:13:53 | 2.65 | 742 | 0 | 0 | 0 | 17.9567 | 24.7 | 6.7433 | 9.9808 | 10.1941 | 10.3106 | 78.675 | 10.1032 | 0.11652 | -0.12013 | 0.090933 | 0.32759 | 615 | 0.29025 | 0.34249 | 395 | 0.18642 | 0.21997 | 70.3852 | 253.562 | 240.0137 | 864.6463 | 2323.3967 | 7922.7828 | 57.9273 | -59.7228 | 197.5321 | -203.6547 | 8120.3149 | 8787.4291 | 10.9438 | 11.8429 | 752.2 | 8296.0542 | 11.0299 | 311.0014
| 17:14:04 | 24.91 | 35.58 | 24.01 | 18.71 | 18.06 | 17.78 | 17.26 | 16.96 | 18.89 | 19.08 | 17.2 | 13.5 | 12.12 | 65.93 | 41.96 | 40.71 | 149.6 | 370.65 | 54.18 | 52.49 | 28.53 | 76.56 | 80.79 | 70.25 | 0 | 0 | 10.37 | 10.4 | 10.14 | 9.87 | -1 | -1 | -1 | -1 | 381.05 | 764 | 17:14:04 | 2.8333 | 764 | 0 | 0 | 0 | 17.9433 | 24.91 | 6.9667 | 10.0946 | 10.3248 | 10.3453 | 78.675 | 10.0945 | 0.020472 | -0.085431 | 0.23029 | 0.3362 | 615 | 0.29025 | 0.34249 | 395 | 0.18642 | 0.21997 | 178.2556 | 260.228 | 607.8515 | 887.3774 | 2400.3456 | 8185.1785 | 10.1776 | -42.4713 | 34.7056 | -144.8273 | 8219.8841 | 9072.5558 | 10.759 | 11.8751 | 753.4 | 8283.391 | 10.9961 | 272.4902
| 17:14:15 | 24.87 | 35.69 | 23.84 | 18.73 | 18.06 | 17.85 | 17.33 | 17.02 | 18.87 | 19.08 | 17.15 | 13.61 | 12.17 | 66.02 | 42.06 | 40.64 | 149.34 | 371.81 | 54.4 | 52.7 | 28.43 | 76.76 | 81.11 | 70.45 | 0 | 0 | 10.39 | 10.42 | 10.08 | 9.92 | -1 | -1 | -1 | -1 | 381.05 | 764 | 17:14:15 | 3.0167 | 764 | 0 | 0 | 0 | 17.9767 | 24.87 | 6.8933 | 10.0316 | 10.3417 | 10.3721 | 78.935 | 10.1501 | 0.030393 | -0.058637 | 0.19165 | 0.28068 | 615 | 0.29025 | 0.34249 | 395 | 0.18642 | 0.21997 | 148.3424 | 217.2545 | 505.8476 | 740.8377 | 2375.0788 | 8099.0187 | 15.1096 | -29.151 | 51.5236 | -99.405 | 8150.5423 | 8839.8564 | 10.6682 | 11.5705 | 754.2 | 8232.6324 | 10.9181 | 204.1081
| 17:14:27 | 24.84 | 35.77 | 23.8 | 18.82 | 18.03 | 17.85 | 17.38 | 17.04 | 18.91 | 19.1 | 17.26 | 13.53 | 12.21 | 66.09 | 42.13 | 40.85 | 149.63 | 373.04 | 54.4 | 52.5 | 28.32 | 76.76 | 81 | 70.55 | 0 | 0 | 10.33 | 10.43 | 10.05 | 9.94 | -1 | -1 | -1 | -1 | 381.05 | 747 | 17:14:27 | 3.2167 | 747 | 0 | 0 | 0 | 18.005 | 24.84 | 6.835 | 10.0071 | 10.2831 | 10.3776 | 78.88 | 10.1613 | 0.094553 | -0.053108 | 0.12181 | 0.26947 | 615 | 0.29025 | 0.34249 | 395 | 0.18642 | 0.21997 | 94.2876 | 208.5814 | 321.5207 | 711.2624 | 2354.9802 | 8030.4825 | 47.0061 | -26.4021 | 160.2909 | -90.031 | 8190.7734 | 8741.7449 | 10.9649 | 11.7025 | 751.6 | 8208.279 | 10.9236 | 158.6064
| 17:14:38 | 24.75 | 35.89 | 23.93 | 18.72 | 18.02 | 17.85 | 17.37 | 17.02 | 18.9 | 19.09 | 16.95 | 13.54 | 12.2 | 66.14 | 42.24 | 40.99 | 149.86 | 373.3 | 54.19 | 52.28 | 28 | 76.66 | 81.11 | 70.45 | 0 | 0 | 10.23 | 10.38 | 10.1 | 9.92 | -1 | -1 | -1 | -1 | 381.05 | 747 | 17:14:38 | 3.4 | 747 | 0 | 0 | 0 | 17.98 | 24.75 | 6.77 | 10.0473 | 10.1835 | 10.3275 | 78.885 | 10.1457 | 0.14395 | -0.10328 | 0.037816 | 0.28505 | 615 | 0.29025 | 0.34249 | 395 | 0.18642 | 0.21997 | 29.2711 | 220.6384 | 99.8144 | 752.3768 | 2332.5846 | 7954.1136 | 71.5644 | -51.3462 | 244.0348 | -175.0907 | 8198.1484 | 8706.4905 | 10.9748 | 11.6553 | 752.8 | 8175.9326 | 10.8621 | 137.6174
| 17:14:48 | 24.79 | 35.91 | 24.04 | 18.66 | 18.09 | 17.82 | 17.32 | 17.03 | 18.87 | 19.1 | 16.76 | 13.45 | 12.18 | 66.19 | 42.25 | 41.11 | 149.43 | 374.2 | 54.2 | 52.7 | 27.88 | 76.76 | 81.01 | 70.55 | 0 | 0 | 10.34 | 10.34 | 10.16 | 9.92 | -1 | -1 | -1 | -1 | 381.06 | 768 | 17:14:48 | 3.5667 | 768 | 0 | 0 | 0 | 17.965 | 24.79 | 6.825 | 10.1169 | 10.2916 | 10.294 | 78.885 | 10.136 | 0.0023297 | -0.13678 | 0.15567 | 0.29478 | 615 | 0.29025 | 0.34249 | 395 | 0.18642 | 0.21997 | 120.4903 | 228.168 | 410.872 | 778.0528 | 2351.5347 | 8018.7334 | 1.1582 | -68.0006 | 3.9495 | -231.882 | 8022.6829 | 8796.7862 | 10.4462 | 11.4541 | 758 | 8156.4062 | 10.7626 | 98.9009
| 17:14:59 | 24.89 | 35.96 | 24.02 | 18.72 | 18.07 | 17.82 | 17.34 | 17.02 | 18.85 | 19.1 | 16.88 | 13.48 | 12.19 | 66.23 | 42.31 | 41.12 | 150.39 | 374.68 | 53.99 | 52.38 | 27.66 | 76.56 | 80.8 | 70.34 | 0 | 0 | 10.33 | 10.29 | 10.11 | 9.89 | -1 | -1 | -1 | -1 | 381.06 | 769 | 17:14:59 | 3.75 | 769 | 0 | 0 | 0 | 17.97 | 24.89 | 6.92 | 10.0648 | 10.2904 | 10.2399 | 78.68 | 10.1124 | -0.050412 | -0.1908 | 0.17793 | 0.31831 | 615 | 0.29025 | 0.34249 | 395 | 0.18642 | 0.21997 | 137.7206 | 246.3854 | 469.6273 | 840.1742 | 2384.2667 | 8130.3495 | -25.0621 | -94.855 | -85.4619 | -323.4554 | 8044.8876 | 8970.5237 | 10.4615 | 11.6652 | 759 | 8121.4069 | 10.7031 | 74.8674
| 17:15:09 | 24.73 | 35.99 | 23.88 | 18.66 | 18.11 | 17.85 | 17.36 | 17.04 | 18.83 | 19.07 | 16.81 | 13.55 | 12.21 | 66.32 | 42.35 | 41.14 | 150 | 375.12 | 53.99 | 52.49 | 27.67 | 76.76 | 81.01 | 70.54 | 0 | 0 | 10.26 | 10.31 | 10.03 | 9.92 | -1 | -1 | -1 | -1 | 381.06 | 770 | 17:15:09 | 3.9167 | 770 | 0 | 0 | 0 | 17.975 | 24.73 | 6.755 | 9.9791 | 10.2127 | 10.2609 | 78.885 | 10.1425 | 0.048195 | -0.16987 | 0.070229 | 0.28829 | 615 | 0.29025 | 0.34249 | 395 | 0.18642 | 0.21997 | 54.3597 | 223.149 | 185.3667 | 760.9379 | 2327.4164 | 7936.49 | 23.9599 | -84.4495 | 81.7032 | -287.9727 | 8018.1932 | 8697.428 | 10.4132 | 11.2954 | 760.2 | 8094.9371 | 10.6521 | 80.9033
| 17:15:20 | 24.84 | 36.05 | 24.09 | 18.74 | 18.07 | 17.88 | 17.38 | 17.03 | 18.89 | 19.12 | 16.81 | 13.54 | 12.25 | 66.4 | 42.4 | 41.2 | 149.7 | 375.19 | 53.99 | 52.6 | 27.67 | 76.87 | 81.02 | 70.64 | 0 | 0 | 10.35 | 10.34 | 10.15 | 9.95 | -1 | -1 | -1 | -1 | 381.07 | 772 | 17:15:20 | 4.1 | 772 | 0 | 0 | 0 | 17.9983 | 24.84 | 6.8417 | 10.1079 | 10.303 | 10.2953 | 78.945 | 10.1654 | -0.0077093 | -0.13546 | 0.13755 | 0.2653 | 615 | 0.29025 | 0.34249 | 395 | 0.18642 | 0.21997 | 106.4672 | 205.3489 | 363.053 | 700.2398 | 2357.2772 | 8038.3152 | -3.8326 | -67.342 | -13.0692 | -229.6364 | 8025.246 | 8738.555 | 10.3954 | 11.3194 | 765.2 | 8061.8316 | 10.5382 | 46.2313
| 17:15:30 | 24.8 | 36.12 | 23.98 | 18.66 | 18.08 | 17.85 | 17.38 | 17.02 | 18.93 | 19.11 | 16.69 | 13.48 | 12.22 | 66.44 | 42.47 | 41.34 | 149.47 | 375.43 | 53.79 | 52.6 | 27.23 | 76.76 | 80.92 | 70.76 | 0 | 0 | 10.32 | 10.22 | 10.04 | 9.94 | -1 | -1 | -1 | -1 | 381.07 | 772 | 17:15:30 | 4.2667 | 772 | 0 | 0 | 0 | 17.9867 | 24.8 | 6.8133 | 10.0025 | 10.278 | 10.1685 | 78.84 | 10.1441 | -0.1095 | -0.26222 | 0.13388 | 0.28661 | 615 | 0.29025 | 0.34249 | 395 | 0.18642 | 0.21997 | 103.6285 | 221.8446 | 353.3733 | 756.4902 | 2347.515 | 8005.0262 | -54.4347 | -130.3621 | -185.6222 | -444.5347 | 7819.404 | 8761.5164 | 10.1288 | 11.3491 | 770.2 | 7986.0828 | 10.369 | -39.7001
| 17:15:40 | 24.92 | 36.21 | 24.04 | 18.64 | 18.11 | 17.9 | 17.37 | 17.07 | 18.97 | 19.17 | 16.69 | 13.58 | 12.26 | 66.49 | 42.55 | 41.34 | 149.94 | 376.66 | 54.01 | 52.49 | 27.23 | 76.77 | 81.02 | 70.76 | 0 | 0 | 10.38 | 10.27 | 10.12 | 9.96 | -1 | -1 | -1 | -1 | 381.07 | 774 | 17:15:40 | 4.4333 | 774 | 0 | 0 | 0 | 18.01 | 24.92 | 6.91 | 10.0809 | 10.3311 | 10.2197 | 78.895 | 10.1665 | -0.11145 | -0.21109 | 0.16462 | 0.26426 | 615 | 0.29025 | 0.34249 | 395 | 0.18642 | 0.21997 | 127.4216 | 204.546 | 434.5077 | 697.502 | 2380.8212 | 8118.6004 | -55.406 | -104.9412 | -188.9345 | -357.8495 | 7929.666 | 8816.1024 | 10.245 | 11.3903 | 771.4 | 7967.4794 | 10.3288 | -78.2769
| 17:15:51 | 25.02 | 36.22 | 23.96 | 18.72 | 18.14 | 17.91 | 17.4 | 17.03 | 18.95 | 19.16 | 16.6 | 13.59 | 12.31 | 66.53 | 42.58 | 41.4 | 149.53 | 377.49 | 54 | 52.91 | 27.23 | 77.17 | 81.32 | 70.76 | 0 | 0 | 10.52 | 10.28 | 10.08 | 10 | -1 | -1 | -1 | -1 | 381.07 | 773 | 17:15:51 | 4.6167 | 773 | 0 | 0 | 0 | 18.025 | 25.02 | 6.995 | 10.0299 | 10.4785 | 10.2254 | 79.245 | 10.2221 | -0.25314 | -0.20539 | 0.25637 | 0.20862 | 615 | 0.29025 | 0.34249 | 395 | 0.18642 | 0.21997 | 198.4365 | 161.4783 | 676.6686 | 550.6411 | 2410.1078 | 8218.4675 | -125.8471 | -102.1097 | -429.1386 | -348.1941 | 7789.3289 | 8769.1086 | 10.0768 | 11.3443 | 772.2 | 7916.3676 | 10.2518 | -147.0123
| 17:16:03 | 25.04 | 36.25 | 24.12 | 18.7 | 18.13 | 17.87 | 17.49 | 17.17 | 18.94 | 19.16 | 17.17 | 13.6 | 12.28 | 66.59 | 42.64 | 41.45 | 149.82 | 377.41 | 54.21 | 52.91 | 27.24 | 76.87 | 81.11 | 70.76 | 0 | 0 | 10.54 | 10.3 | 10.22 | 9.99 | -1 | -1 | -1 | -1 | 381.08 | 775 | 17:16:03 | 4.8167 | 775 | 0 | 0 | 0 | 18.05 | 25.04 | 6.99 | 10.1683 | 10.4912 | 10.2463 | 78.99 | 10.205 | -0.24492 | -0.18447 | 0.28621 | 0.22576 | 615 | 0.29025 | 0.34249 | 395 | 0.18642 | 0.21997 | 221.5379 | 174.7426 | 755.4441 | 595.8724 | 2408.385 | 8212.5929 | -121.7615 | -91.706 | -415.2068 | -312.7176 | 7797.3862 | 8808.4653 | 10.0611 | 11.3658 | 773.2 | 7872.2062 | 10.1814 | -246.3942
| 17:16:14 | 24.89 | 36.27 | 24.03 | 18.86 | 18.16 | 17.91 | 17.46 | 17.13 | 19 | 19.19 | 17.06 | 13.59 | 12.3 | 66.62 | 42.72 | 41.47 | 150.51 | 377.4 | 54.01 | 53.12 | 27.02 | 77.07 | 81.23 | 70.76 | 0 | 0 | 10.48 | 10.23 | 10.12 | 10.03 | -1 | -1 | -1 | -1 | 381.08 | 775 | 17:16:14 | 5 | 775 | 0 | 0 | 0 | 18.0867 | 24.89 | 6.8033 | 10.0747 | 10.4382 | 10.1735 | 79.15 | 10.25 | -0.26467 | -0.25725 | 0.18818 | 0.18075 | 615 | 0.29025 | 0.34249 | 395 | 0.18642 | 0.21997 | 145.6591 | 139.9085 | 496.6974 | 477.088 | 2344.0695 | 7993.2771 | -131.5812 | -127.8877 | -448.6918 | -436.0972 | 7544.5853 | 8470.3652 | 9.7349 | 10.9295 | 773.8 | 7776.0741 | 10.0493 | -333.5188
| 17:16:24 | 25.1 | 36.36 | 24.03 | 18.93 | 18.09 | 17.93 | 17.42 | 17.09 | 18.98 | 19.21 | 17.12 | 13.62 | 12.3 | 66.59 | 42.74 | 41.67 | 150.47 | 378.18 | 54.21 | 52.92 | 27.02 | 77.07 | 81.22 | 70.96 | 0 | 0 | 10.58 | 10.27 | 10.16 | 10.03 | -1 | -1 | -1 | -1 | 381.08 | 775 | 17:16:24 | 5.1667 | 775 | 0 | 0 | 0 | 18.0733 | 25.1 | 7.0267 | 10.1126 | 10.5314 | 10.2246 | 79.145 | 10.2406 | -0.30683 | -0.20614 | 0.29083 | 0.19014 | 615 | 0.29025 | 0.34249 | 395 | 0.18642 | 0.21997 | 225.1117 | 147.1751 | 767.631 | 501.8672 | 2421.0184 | 8255.6728 | -152.5392 | -102.4824 | -520.1587 | -349.4649 | 7735.5141 | 8757.54 | 9.9813 | 11.3001 | 774.4 | 7759.2961 | 10.0198 | -400.4261
| 17:16:35 | 24.95 | 36.49 | 24.04 | 18.78 | 18.21 | 17.95 | 17.46 | 17.1 | 18.96 | 19.23 | 17.52 | 13.65 | 12.33 | 66.7 | 42.82 | 41.6 | 150.35 | 379.48 | 54.11 | 52.93 | 27.02 | 77.07 | 81.23 | 70.96 | 0 | 0 | 10.49 | 10.35 | 10.15 | 10.03 | -1 | -1 | -1 | -1 | 381.08 | 776 | 17:16:35 | 5.35 | 776 | 0 | 0 | 0 | 18.0767 | 24.95 | 6.8733 | 10.0999 | 10.4381 | 10.2988 | 79.15 | 10.2434 | -0.13931 | -0.13193 | 0.19469 | 0.1873 | 615 | 0.29025 | 0.34249 | 395 | 0.18642 | 0.21997 | 150.6935 | 144.9772 | 513.8647 | 494.3723 | 2368.1878 | 8075.5206 | -69.258 | -65.5866 | -236.1698 | -223.6503 | 7839.3508 | 8569.8928 | 10.1023 | 11.0437 | 774.8 | 7741.233 | 9.9913 | -409.8731
| 17:16:46 | 24.95 | 36.56 | 24.03 | 18.83 | 18.21 | 17.9 | 17.41 | 17.07 | 18.98 | 19.25 | 17.5 | 13.65 | 12.31 | 66.76 | 42.9 | 41.71 | 150.19 | 380.29 | 54.02 | 52.72 | 26.81 | 76.77 | 81.02 | 70.86 | 0 | 0 | 10.44 | 10.31 | 10.12 | 10 | -1 | -1 | -1 | -1 | 381.08 | 778 | 17:16:46 | 5.5333 | 778 | 0 | 0 | 0 | 18.0667 | 24.95 | 6.8833 | 10.0766 | 10.396 | 10.2573 | 78.895 | 10.2034 | -0.13873 | -0.17345 | 0.19265 | 0.22737 | 615 | 0.29025 | 0.34249 | 395 | 0.18642 | 0.21997 | 149.115 | 175.9898 | 508.4822 | 600.1253 | 2371.6333 | 8087.2696 | -68.9673 | -86.2283 | -235.1784 | -294.0387 | 7852.0912 | 8687.3949 | 10.0927 | 11.1663 | 775.8 | 7753.7855 | 9.9945 | -371.0811
| 17:16:58 | 24.93 | 36.57 | 24.04 | 18.73 | 18.23 | 17.97 | 17.49 | 17.09 | 18.99 | 19.23 | 17.11 | 13.68 | 12.38 | 66.85 | 42.94 | 41.88 | 150.59 | 380.03 | 53.91 | 52.82 | 26.81 | 76.98 | 81.23 | 70.86 | 0 | 0 | 10.45 | 10.32 | 10.11 | 10.03 | -1 | -1 | -1 | -1 | 381.09 | 780 | 17:16:58 | 5.7333 | 780 | 0 | 0 | 0 | 18.0833 | 24.93 | 6.8467 | 10.0619 | 10.4034 | 10.263 | 79.105 | 10.2419 | -0.14045 | -0.16775 | 0.16156 | 0.18886 | 615 | 0.29025 | 0.34249 | 395 | 0.18642 | 0.21997 | 125.0545 | 146.1824 | 426.4358 | 498.482 | 2358.9999 | 8044.1897 | -69.8236 | -83.3936 | -238.0985 | -284.372 | 7806.0913 | 8542.6717 | 10.0078 | 10.9521 | 776.8 | 7755.5265 | 9.9838 | -335.6594
| 17:17:08 | 25.03 | 36.55 | 24.04 | 18.85 | 18.2 | 17.95 | 17.44 | 17.09 | 19.09 | 19.23 | 16.96 | 13.63 | 12.35 | 66.92 | 42.94 | 41.91 | 150.28 | 379.89 | 54.03 | 52.93 | 26.6 | 76.98 | 81.13 | 70.87 | 0 | 0 | 10.54 | 10.22 | 10.13 | 10.03 | -1 | -1 | -1 | -1 | 381.09 | 780 | 17:17:08 | 5.9 | 780 | 0 | 0 | 0 | 18.1033 | 25.03 | 6.9267 | 10.0847 | 10.4889 | 10.17 | 79.055 | 10.2484 | -0.31889 | -0.26076 | 0.24048 | 0.18235 | 615 | 0.29025 | 0.34249 | 395 | 0.18642 | 0.21997 | 186.1389 | 141.1441 | 634.7336 | 481.3013 | 2386.5637 | 8138.1822 | -158.5341 | -129.6349 | -540.6012 | -442.0552 | 7597.5811 | 8619.4835 | 9.7405 | 11.0506 | 777.8 | 7766.1257 | 9.9849 | -354.0413
| 17:17:18 | 25.07 | 36.57 | 24.05 | 18.81 | 18.16 | 17.94 | 17.47 | 17.09 | 19.08 | 19.24 | 17.3 | 13.73 | 12.35 | 67 | 42.95 | 41.68 | 150.31 | 380.93 | 53.61 | 52.73 | 26.48 | 76.98 | 81.23 | 70.77 | 0 | 0 | 10.52 | 10.19 | 10.05 | 10.03 | -1 | -1 | -1 | -1 | 381.09 | 779 | 17:17:18 | 6.0667 | 779 | 0 | 0 | 0 | 18.0917 | 25.07 | 6.9783 | 10.0111 | 10.4739 | 10.1346 | 79.105 | 10.2473 | -0.33932 | -0.29613 | 0.22659 | 0.1834 | 615 | 0.29025 | 0.34249 | 395 | 0.18642 | 0.21997 | 175.3878 | 141.9596 | 598.0725 | 484.0821 | 2404.3653 | 8198.8857 | -168.689 | -147.2188 | -575.2294 | -502.0161 | 7623.6563 | 8682.9678 | 9.7865 | 11.1463 | 778.6 | 7743.7541 | 9.9459 | -365.0555
| 17:17:29 | 25.05 | 36.59 | 24.18 | 18.94 | 18.24 | 17.96 | 17.46 | 17.11 | 19.16 | 19.26 | 17.49 | 13.68 | 12.32 | 67.04 | 42.99 | 41.74 | 150.31 | 381.4 | 54.03 | 52.73 | 26.6 | 77.19 | 81.45 | 70.98 | 0 | 0 | 10.51 | 10.25 | 10.22 | 10.09 | -1 | -1 | -1 | -1 | 381.1 | 780 | 17:17:29 | 6.25 | 780 | 0 | 0 | 0 | 18.145 | 25.05 | 6.905 | 10.1712 | 10.4612 | 10.1926 | 79.32 | 10.3107 | -0.26863 | -0.23813 | 0.15052 | 0.12002 | 615 | 0.29025 | 0.34249 | 395 | 0.18642 | 0.21997 | 116.5056 | 92.8957 | 397.2841 | 316.7742 | 2379.0985 | 8112.7259 | -133.5489 | -118.3847 | -455.4016 | -403.692 | 7657.3243 | 8429.5001 | 9.8171 | 10.8071 | 779.4 | 7707.3488 | 9.8889 | -408.9018
| 17:17:39 | 25.19 | 36.72 | 24.17 | 18.84 | 18.21 | 17.99 | 17.42 | 17.07 | 19.03 | 19.31 | 17.59 | 13.66 | 12.38 | 67.11 | 43.05 | 41.91 | 150.35 | 381.67 | 53.82 | 52.32 | 26.38 | 76.79 | 81.03 | 70.88 | 0 | 0 | 10.51 | 10.23 | 10.17 | 10.03 | -1 | -1 | -1 | -1 | 381.1 | 780 | 17:17:39 | 6.4167 | 780 | 0 | 0 | 0 | 18.0933 | 25.19 | 7.0967 | 10.1248 | 10.4669 | 10.1802 | 78.91 | 10.2228 | -0.28675 | -0.25058 | 0.24416 | 0.20799 | 615 | 0.29025 | 0.34249 | 395 | 0.18642 | 0.21997 | 188.9867 | 160.9907 | 644.4447 | 548.9783 | 2445.1367 | 8337.9162 | -142.5535 | -124.5723 | -486.1074 | -424.7916 | 7851.8088 | 8886.8945 | 10.0664 | 11.3935 | 779.8 | 7707.2923 | 9.8837 | -459.0876
| 17:17:50 | 25.1 | 36.76 | 24.25 | 18.81 | 18.25 | 17.97 | 17.43 | 17.07 | 19 | 19.28 | 17.51 | 13.62 | 12.37 | 67.18 | 43.13 | 41.93 | 150.44 | 381.63 | 53.83 | 52.94 | 26.39 | 76.89 | 81.23 | 70.78 | 0 | 0 | 10.58 | 10.26 | 10.22 | 10.03 | -1 | -1 | -1 | -1 | 381.1 | 781 | 17:17:50 | 6.6 | 781 | 0 | 0 | 0 | 18.0883 | 25.1 | 7.0117 | 10.1762 | 10.5355 | 10.2067 | 79.06 | 10.2392 | -0.32876 | -0.22402 | 0.29625 | 0.19151 | 615 | 0.29025 | 0.34249 | 395 | 0.18642 | 0.21997 | 229.3039 | 148.2344 | 781.9262 | 505.4791 | 2415.8502 | 8238.0492 | -163.4395 | -111.3704 | -557.3286 | -379.7732 | 7680.7206 | 8743.5284 | 9.8345 | 11.1953 | 780 | 7682.2182 | 9.849 | -522.9336
| 17:18:03 | 25.06 | 36.83 | 24.36 | 18.9 | 18.24 | 17.97 | 17.44 | 17.12 | 19.06 | 19.27 | 17.35 | 13.76 | 12.41 | 67.21 | 43.17 | 42.04 | 150.58 | 382.03 | 53.62 | 52.42 | 26.38 | 76.79 | 81.22 | 70.78 | 0 | 0 | 10.45 | 10.29 | 10.25 | 10.04 | -1 | -1 | -1 | -1 | 381.1 | 783 | 17:18:03 | 6.8167 | 783 | 0 | 0 | 0 | 18.1217 | 25.06 | 6.9383 | 10.204 | 10.405 | 10.2425 | 79.005 | 10.2538 | -0.16253 | -0.18825 | 0.15121 | 0.17693 | 615 | 0.29025 | 0.34249 | 395 | 0.18642 | 0.21997 | 117.0401 | 136.9524 | 399.1068 | 467.0078 | 2390.5834 | 8151.8895 | -80.7991 | -93.5883 | -275.5251 | -319.1362 | 7876.3644 | 8618.8972 | 10.0592 | 11.0075 | 780.6 | 7737.9749 | 9.9127 | -469.9184
| 17:18:16 | 25.18 | 36.81 | 24.5 | 18.93 | 18.33 | 18.04 | 17.53 | 17.16 | 19.14 | 19.34 | 17.14 | 13.78 | 12.49 | 67.28 | 43.2 | 41.99 | 151.1 | 382.8 | 53.63 | 52.53 | 26.16 | 77 | 81.45 | 70.88 | 0 | 0 | 10.55 | 10.19 | 10.34 | 10.11 | -1 | -1 | -1 | -1 | 381.1 | 783 | 17:18:16 | 7.0333 | 783 | 0 | 0 | 0 | 18.1883 | 25.18 | 6.9917 | 10.2933 | 10.5033 | 10.1444 | 79.225 | 10.3267 | -0.35886 | -0.28632 | 0.17656 | 0.10403 | 615 | 0.29025 | 0.34249 | 395 | 0.18642 | 0.21997 | 136.6604 | 80.5195 | 466.012 | 274.5714 | 2408.9593 | 8214.5511 | -178.4024 | -142.3444 | -608.352 | -485.3943 | 7606.1991 | 8489.1225 | 9.7142 | 10.8418 | 781.4 | 7734.4834 | 9.8983 | -476.5429
| 17:18:27 | 25.13 | 36.77 | 24.38 | 18.93 | 18.38 | 18.12 | 17.64 | 17.22 | 19.15 | 19.35 | 17.15 | 13.85 | 12.51 | 67.38 | 43.19 | 42.04 | 152.08 | 382.99 | 54.05 | 52.94 | 26.39 | 77.2 | 81.66 | 71.18 | 0 | 0 | 10.61 | 10.26 | 10.34 | 10.17 | -1 | -1 | -1 | -1 | 381.11 | 781 | 17:18:27 | 7.2167 | 781 | 0 | 0 | 0 | 18.24 | 25.13 | 6.89 | 10.2997 | 10.5546 | 10.2124 | 79.43 | 10.3881 | -0.34225 | -0.21836 | 0.16654 | 0.042645 | 615 | 0.29025 | 0.34249 | 395 | 0.18642 | 0.21997 | 128.91 | 33.0084 | 439.5831 | 112.5586 | 2373.9303 | 8095.1023 | -170.1493 | -108.554 | -580.2093 | -370.1691 | 7514.8931 | 8207.6609 | 9.6221 | 10.5092 | 781.6 | 7705.9972 | 9.8593 | -501.5045
| 17:18:37 | 25.05 | 36.82 | 24.24 | 18.87 | 18.4 | 18.12 | 17.56 | 17.15 | 19.06 | 19.35 | 17.24 | 13.81 | 12.48 | 67.36 | 43.21 | 42.07 | 150.93 | 382.79 | 54.26 | 52.73 | 26.4 | 77.22 | 81.66 | 71.19 | 0 | 0 | 10.51 | 10.29 | 10.3 | 10.14 | -1 | -1 | -1 | -1 | 381.11 | 783 | 17:18:37 | 7.3833 | 783 | 0 | 0 | 0 | 18.1933 | 25.05 | 6.8567 | 10.2526 | 10.4612 | 10.2447 | 79.44 | 10.3585 | -0.21655 | -0.18604 | 0.10273 | 0.072228 | 615 | 0.29025 | 0.34249 | 395 | 0.18642 | 0.21997 | 79.5165 | 55.9065 | 271.1513 | 190.6413 | 2362.4454 | 8055.9388 | -107.6542 | -92.4901 | -367.1008 | -315.3912 | 7688.838 | 8246.5801 | 9.8197 | 10.532 | 782.2 | 7673.403 | 9.8099 | -477.7032
| 17:18:48 | 24.93 | 36.94 | 24.23 | 18.97 | 18.32 | 18.08 | 17.58 | 17.2 | 19.19 | 19.4 | 17.39 | 13.76 | 12.49 | 67.43 | 43.26 | 42.16 | 151.18 | 384 | 54.05 | 52.73 | 26.28 | 77.01 | 81.46 | 71.28 | 0 | 0 | 10.43 | 10.31 | 10.25 | 10.15 | -1 | -1 | -1 | -1 | 381.11 | 786 | 17:18:48 | 7.5667 | 786 | 0 | 0 | 0 | 18.2233 | 24.93 | 6.7067 | 10.2061 | 10.3854 | 10.2654 | 79.235 | 10.3512 | -0.11998 | -0.1653 | 0.034274 | 0.079593 | 615 | 0.29025 | 0.34249 | 395 | 0.18642 | 0.21997 | 26.5293 | 61.6072 | 90.465 | 210.0805 | 2310.7633 | 7879.7029 | -59.6482 | -82.1779 | -203.4005 | -280.2267 | 7676.3024 | 8089.7834 | 9.7663 | 10.2923 | 783.2 | 7672.5194 | 9.7963 | -406.9175
| 17:18:59 | 25.05 | 36.91 | 24.19 | 19.04 | 18.32 | 18.07 | 17.5 | 17.17 | 19.15 | 19.37 | 17.16 | 13.87 | 12.45 | 67.51 | 43.32 | 42.29 | 150.28 | 383.43 | 53.63 | 52.32 | 25.95 | 76.81 | 81.25 | 70.79 | 0 | 0 | 10.42 | 10.17 | 10.14 | 10.1 | -1 | -1 | -1 | -1 | 381.11 | 785 | 17:18:59 | 7.75 | 785 | 0 | 0 | 0 | 18.2083 | 25.05 | 6.8417 | 10.1008 | 10.3785 | 10.1176 | 79.03 | 10.314 | -0.26094 | -0.31314 | 0.064505 | 0.1167 | 615 | 0.29025 | 0.34249 | 395 | 0.18642 | 0.21997 | 49.9289 | 90.3302 | 170.2575 | 308.0258 | 2357.2772 | 8038.3152 | -129.7263 | -155.6751 | -442.3667 | -530.852 | 7595.9485 | 8346.341 | 9.6764 | 10.6323 | 783.6 | 7616.4362 | 9.7197 | -440.2859
| 17:19:09 | 25.15 | 37.09 | 24.39 | 19.07 | 18.31 | 18.07 | 17.54 | 17.19 | 19.13 | 19.38 | 17.34 | 13.77 | 12.45 | 67.64 | 43.45 | 42.26 | 150.63 | 385.47 | 53.64 | 52.53 | 25.95 | 76.81 | 81.25 | 70.8 | 0 | 0 | 10.53 | 10.27 | 10.27 | 10.11 | -1 | -1 | -1 | -1 | 381.11 | 787 | 17:19:09 | 7.9167 | 787 | 0 | 0 | 0 | 18.2183 | 25.15 | 6.9317 | 10.2266 | 10.4842 | 10.219 | 79.03 | 10.3206 | -0.26523 | -0.21176 | 0.16358 | 0.11011 | 615 | 0.29025 | 0.34249 | 395 | 0.18642 | 0.21997 | 126.619 | 85.2312 | 431.7707 | 290.6383 | 2388.2864 | 8144.0567 | -131.8572 | -105.2748 | -449.6331 | -358.9871 | 7694.4237 | 8434.6951 | 9.7769 | 10.7175 | 784.4 | 7634.0811 | 9.7323 | -408.5421
| 17:19:19 | 25.12 | 37 | 24.17 | 18.97 | 18.37 | 18.07 | 17.56 | 17.19 | 19.11 | 19.34 | 17.4 | 13.83 | 12.48 | 67.69 | 43.38 | 42.29 | 151.09 | 384.95 | 53.64 | 52.63 | 25.96 | 76.82 | 81.25 | 70.9 | 0 | 0 | 10.53 | 10.22 | 10.13 | 10.1 | -1 | -1 | -1 | -1 | 381.11 | 786 | 17:19:19 | 8.0833 | 786 | 0 | 0 | 0 | 18.2117 | 25.12 | 6.9083 | 10.0904 | 10.4854 | 10.1722 | 79.035 | 10.3169 | -0.31328 | -0.25858 | 0.16854 | 0.11384 | 615 | 0.29025 | 0.34249 | 395 | 0.18642 | 0.21997 | 130.4563 | 88.1172 | 444.8559 | 300.4798 | 2380.247 | 8116.6423 | -155.7439 | -128.5506 | -531.0869 | -438.3575 | 7585.5554 | 8417.1221 | 9.6508 | 10.7088 | 785.4 | 7648.2136 | 9.738 | -398.7176
| 17:19:30 | 24.96 | 37.06 | 24.22 | 18.99 | 18.39 | 18.1 | 17.57 | 17.18 | 19.16 | 19.41 | 17.43 | 13.81 | 12.48 | 67.75 | 43.42 | 42.21 | 150.96 | 385.18 | 53.64 | 52.53 | 25.96 | 76.81 | 81.25 | 71 | 0 | 0 | 10.41 | 10.26 | 10.17 | 10.13 | -1 | -1 | -1 | -1 | 381.12 | 786 | 17:19:30 | 8.2667 | 786 | 0 | 0 | 0 | 18.2317 | 24.96 | 6.7283 | 10.1212 | 10.3642 | 10.206 | 79.03 | 10.3294 | -0.15819 | -0.22472 | 0.034794 | 0.10132 | 615 | 0.29025 | 0.34249 | 395 | 0.18642 | 0.21997 | 26.932 | 78.428 | 91.8382 | 267.4395 | 2318.2285 | 7905.1592 | -78.6445 | -111.7192 | -268.1778 | -380.9623 | 7636.9814 | 8172.5987 | 9.7163 | 10.3977 | 786 | 7637.8423 | 9.7173 | -378.933
| 17:19:40 | 25.22 | 37.08 | 24.27 | 18.96 | 18.38 | 18.11 | 17.56 | 17.2 | 19.12 | 19.4 | 17.57 | 13.86 | 12.5 | 67.77 | 43.42 | 42.38 | 151.11 | 385.01 | 53.64 | 52.54 | 25.85 | 76.82 | 81.25 | 70.99 | 0 | 0 | 10.58 | 10.22 | 10.2 | 10.12 | -1 | -1 | -1 | -1 | 381.12 | 785 | 17:19:40 | 8.4333 | 785 | 0 | 0 | 0 | 18.2217 | 25.22 | 6.9983 | 10.1521 | 10.5308 | 10.1733 | 79.035 | 10.3235 | -0.35745 | -0.25742 | 0.20728 | 0.10725 | 615 | 0.29025 | 0.34249 | 395 | 0.18642 | 0.21997 | 160.4435 | 83.017 | 547.1125 | 283.0878 | 2411.2562 | 8222.3838 | -177.7022 | -127.9729 | -605.9645 | -436.3877 | 7616.4193 | 8505.4716 | 9.7024 | 10.835 | 785.8 | 7625.8657 | 9.7046 | -459.4458
| 17:19:51 | 25.21 | 37.06 | 24.4 | 18.97 | 18.44 | 18.11 | 17.57 | 17.19 | 19.12 | 19.38 | 17.37 | 13.84 | 12.5 | 67.85 | 43.45 | 42.37 | 151.44 | 384.9 | 53.65 | 52.33 | 25.85 | 76.82 | 81.25 | 70.9 | 0 | 0 | 10.53 | 10.21 | 10.28 | 10.12 | -1 | -1 | -1 | -1 | 381.12 | 770 | 17:19:51 | 8.6167 | 770 | 0 | 0 | 0 | 18.2333 | 25.21 | 6.9767 | 10.2347 | 10.4816 | 10.1621 | 79.035 | 10.3312 | -0.31956 | -0.26867 | 0.15044 | 0.09956 | 615 | 0.29025 | 0.34249 | 395 | 0.18642 | 0.21997 | 116.4487 | 77.0629 | 397.0901 | 262.7846 | 2403.7911 | 8196.9275 | -158.8664 | -133.5698 | -541.7343 | -455.473 | 7655.1932 | 8459.7121 | 9.9418 | 10.9866 | 782.8 | 7637.7146 | 9.7577 | -479.3193
| 17:20:01 | 25.29 | 37.14 | 24.32 | 18.97 | 18.4 | 18.12 | 17.6 | 17.22 | 19.16 | 19.38 | 17.51 | 13.8 | 12.53 | 67.92 | 43.46 | 42.33 | 151.32 | 385.77 | 53.65 | 52.44 | 25.86 | 76.82 | 81.25 | 70.79 | 0 | 0 | 10.6 | 10.26 | 10.23 | 10.12 | -1 | -1 | -1 | -1 | 381.13 | 768 | 17:20:01 | 8.7833 | 768 | 0 | 0 | 0 | 18.245 | 25.29 | 7.045 | 10.185 | 10.555 | 10.2112 | 79.035 | 10.3389 | -0.34382 | -0.21956 | 0.21612 | 0.091863 | 615 | 0.29025 | 0.34249 | 395 | 0.18642 | 0.21997 | 167.2853 | 71.105 | 570.4429 | 242.4679 | 2427.3351 | 8277.2128 | -170.9286 | -109.1542 | -582.8665 | -372.2158 | 7694.3463 | 8519.6806 | 10.0187 | 11.0933 | 779 | 7637.6991 | 9.806 | -505.966
| 17:20:12 | 25.37 | 37.14 | 24.32 | 19.13 | 18.42 | 18.15 | 17.64 | 17.27 | 19.21 | 19.42 | 17.53 | 13.79 | 12.58 | 67.97 | 43.51 | 42.47 | 151.75 | 385.94 | 53.85 | 52.76 | 25.86 | 77.03 | 81.57 | 71.1 | 0 | 0 | 10.72 | 10.26 | 10.27 | 10.19 | -1 | -1 | -1 | -1 | 381.13 | 768 | 17:20:12 | 8.9667 | 768 | 0 | 0 | 0 | 18.3033 | 25.37 | 7.0667 | 10.2236 | 10.672 | 10.2112 | 79.3 | 10.4128 | -0.46084 | -0.21956 | 0.2592 | 0.017922 | 615 | 0.29025 | 0.34249 | 395 | 0.18642 | 0.21997 | 200.6312 | 13.872 | 684.1525 | 47.3036 | 2434.8003 | 8302.6691 | -229.1052 | -109.1542 | -781.2489 | -372.2158 | 7521.4202 | 8349.9726 | 9.7935 | 10.8724 | 775.4 | 7624.8721 | 9.8345 | -555.9984
| 17:20:22 | 25.22 | 37.19 | 24.3 | 19.11 | 18.44 | 18.15 | 17.63 | 17.3 | 19.16 | 19.38 | 17.54 | 13.92 | 12.58 | 68 | 43.58 | 42.49 | 151.31 | 386.63 | 53.64 | 52.76 | 25.86 | 77.03 | 81.57 | 71.2 | 0 | 0 | 10.62 | 10.29 | 10.21 | 10.19 | -1 | -1 | -1 | -1 | 381.13 | 780 | 17:20:22 | 9.1333 | 780 | 0 | 0 | 0 | 18.2983 | 25.22 | 6.9217 | 10.1707 | 10.5756 | 10.2395 | 79.3 | 10.4095 | -0.33615 | -0.19128 | 0.16612 | 0.021244 | 615 | 0.29025 | 0.34249 | 395 | 0.18642 | 0.21997 | 128.5815 | 16.4433 | 438.463 | 56.0718 | 2384.841 | 8132.3077 | -167.115 | -95.0913 | -569.8621 | -324.2612 | 7562.4455 | 8188.3794 | 9.6954 | 10.4979 | 774.2 | 7609.9649 | 9.8304 | -616.3353
| 17:20:32 | 25.36 | 37.19 | 24.26 | 19.12 | 18.52 | 18.17 | 17.67 | 17.29 | 19.25 | 19.46 | 17.64 | 13.85 | 12.61 | 68.11 | 43.56 | 42.55 | 151.6 | 386.5 | 53.85 | 52.56 | 25.75 | 77.04 | 81.47 | 71.2 | 0 | 0 | 10.67 | 10.25 | 10.23 | 10.22 | -1 | -1 | -1 | -1 | 381.13 | 790 | 17:20:32 | 9.3 | 790 | 0 | 0 | 0 | 18.3367 | 25.36 | 7.0233 | 10.1863 | 10.6245 | 10.1952 | 79.255 | 10.429 | -0.42925 | -0.23554 | 0.19548 | 0.0017718 | 615 | 0.29025 | 0.34249 | 395 | 0.18642 | 0.21997 | 151.308 | 1.3715 | 515.9603 | 4.6767 | 2419.8699 | 8251.7565 | -213.4002 | -117.0995 | -727.6945 | -399.3092 | 7524.0619 | 8256.4332 | 9.5241 | 10.4512 | 775.2 | 7591.4934 | 9.7947 | -640.6813
| 17:20:43 | 25.42 | 37.24 | 24.27 | 19.14 | 18.53 | 18.22 | 17.71 | 17.34 | 19.25 | 19.47 | 17.69 | 13.91 | 12.67 | 68.22 | 43.63 | 42.65 | 152.41 | 387.01 | 53.65 | 52.66 | 25.75 | 77.04 | 81.68 | 71.2 | 0 | 0 | 10.73 | 10.28 | 10.2 | 10.24 | -1 | -1 | -1 | -1 | 381.14 | 789 | 17:20:43 | 9.4833 | 789 | 0 | 0 | 0 | 18.365 | 25.42 | 7.055 | 10.154 | 10.6837 | 10.2234 | 79.36 | 10.4619 | -0.46027 | -0.20731 | 0.22178 | -0.03117 | 615 | 0.29025 | 0.34249 | 395 | 0.18642 | 0.21997 | 171.6668 | -24.1265 | 585.3838 | -82.2714 | 2430.7806 | 8288.9618 | -228.8175 | -103.0641 | -780.2676 | -351.4484 | 7508.6942 | 8206.6904 | 9.5167 | 10.4014 | 779 | 7562.1936 | 9.7097 | -688.3879
| 17:20:53 | 25.55 | 37.27 | 24.19 | 19.04 | 18.6 | 18.24 | 17.76 | 17.3 | 19.28 | 19.53 | 17.95 | 13.93 | 12.66 | 68.22 | 43.64 | 42.52 | 151.84 | 387.46 | 54.06 | 52.78 | 25.87 | 77.24 | 81.69 | 71.53 | 0 | 0 | 10.85 | 10.34 | 10.23 | 10.28 | -1 | -1 | -1 | -1 | 381.14 | 789 | 17:20:53 | 9.65 | 789 | 0 | 0 | 0 | 18.37 | 25.55 | 7.18 | 10.1831 | 10.7929 | 10.2889 | 79.465 | 10.4793 | -0.50399 | -0.14183 | 0.31357 | -0.048587 | 615 | 0.29025 | 0.34249 | 395 | 0.18642 | 0.21997 | 242.7169 | -37.6078 | 827.6646 | -128.2426 | 2473.849 | 8435.8251 | -250.555 | -70.5091 | -854.3926 | -240.4359 | 7581.4325 | 8307.5824 | 9.6089 | 10.5293 | 783.2 | 7539.6109 | 9.6277 | -742.6932
| 17:21:04 | 25.31 | 37.28 | 24.34 | 19.18 | 18.53 | 18.24 | 17.68 | 17.28 | 19.21 | 19.49 | 18.1 | 13.91 | 12.62 | 68.26 | 43.68 | 42.57 | 151.92 | 387.58 | 54.27 | 52.88 | 25.87 | 77.06 | 81.68 | 71.41 | 0 | 0 | 10.7 | 10.35 | 10.36 | 10.25 | -1 | -1 | -1 | -1 | 381.14 | 789 | 17:21:04 | 9.8333 | 789 | 0 | 0 | 0 | 18.3533 | 25.31 | 6.9567 | 10.3172 | 10.658 | 10.2946 | 79.37 | 10.4555 | -0.36336 | -0.13614 | 0.2025 | -0.024726 | 615 | 0.29025 | 0.34249 | 395 | 0.18642 | 0.21997 | 156.7404 | -19.1388 | 534.4846 | -65.2635 | 2396.9001 | 8173.4294 | -180.6433 | -67.6802 | -615.9935 | -230.7895 | 7557.4359 | 8108.1659 | 9.5785 | 10.2765 | 787.4 | 7546.814 | 9.5847 | -709.6421
| 17:21:14 | 25.12 | 37.4 | 24.39 | 19.14 | 18.54 | 18.23 | 17.68 | 17.3 | 19.3 | 19.53 | 18.11 | 13.98 | 12.63 | 68.37 | 43.75 | 42.6 | 151.73 | 387.92 | 54.07 | 52.36 | 25.76 | 77.06 | 81.68 | 71.31 | 0 | 0 | 10.48 | 10.37 | 10.36 | 10.26 | -1 | -1 | -1 | -1 | 381.14 | 791 | 17:21:14 | 10 | 791 | 0 | 0 | 0 | 18.365 | 25.12 | 6.755 | 10.3099 | 10.4308 | 10.3183 | 79.37 | 10.4633 | -0.11244 | -0.11243 | -0.032505 | -0.03251 | 615 | 0.29025 | 0.34249 | 395 | 0.18642 | 0.21997 | -25.1601 | -25.1641 | -85.7958 | -85.8095 | 2327.4164 | 7936.49 | -55.8979 | -55.8954 | -190.612 | -190.6032 | 7745.878 | 7850.6805 | 9.7925 | 9.925 | 789.6 | 7583.5005 | 9.6042 | -633.7921
| 17:21:24 | 25.29 | 37.41 | 24.46 | 19.15 | 18.52 | 18.24 | 17.68 | 17.32 | 19.28 | 19.48 | 18.07 | 13.98 | 12.66 | 68.42 | 43.76 | 42.59 | 151.96 | 388.6 | 53.86 | 52.25 | 25.65 | 76.85 | 81.48 | 71.32 | 0 | 0 | 10.56 | 10.33 | 10.36 | 10.23 | -1 | -1 | -1 | -1 | 381.14 | 790 | 17:21:24 | 10.1667 | 790 | 0 | 0 | 0 | 18.365 | 25.29 | 6.925 | 10.313 | 10.5161 | 10.2792 | 79.165 | 10.4358 | -0.23692 | -0.15155 | 0.080337 | -0.005032 | 615 | 0.29025 | 0.34249 | 395 | 0.18642 | 0.21997 | 62.1838 | -3.8949 | 212.0467 | -13.2817 | 2385.9895 | 8136.224 | -117.7808 | -75.34 | -401.6324 | -256.9093 | 7734.5916 | 8122.9423 | 9.7906 | 10.2822 | 789.6 | 7625.6064 | 9.6575 | -568.5796
| 17:21:35 | 25.49 | 37.39 | 24.26 | 19.32 | 18.55 | 18.25 | 17.73 | 17.42 | 19.35 | 19.51 | 18.02 | 14.01 | 12.68 | 68.52 | 43.73 | 42.68 | 151.85 | 387.95 | 53.86 | 52.47 | 25.65 | 77.04 | 81.59 | 71.12 | 0 | 0 | 10.74 | 10.32 | 10.24 | 10.28 | -1 | -1 | -1 | -1 | 381.15 | 789 | 17:21:35 | 10.35 | 789 | 0 | 0 | 0 | 18.4367 | 25.49 | 7.0533 | 10.1882 | 10.6896 | 10.2678 | 79.315 | 10.5038 | -0.42176 | -0.1629 | 0.18583 | -0.073035 | 615 | 0.29025 | 0.34249 | 395 | 0.18642 | 0.21997 | 143.8394 | -56.5312 | 490.4925 | -192.7715 | 2430.2063 | 8287.0036 | -209.6757 | -80.9824 | -714.9942 | -276.1499 | 7572.0094 | 8094.2321 | 9.597 | 10.2588 | 789.6 | 7638.2695 | 9.6735 | -555.525
| 17:21:45 | 25.44 | 37.36 | 24.3 | 19.27 | 18.59 | 18.25 | 17.8 | 17.41 | 19.36 | 19.58 | 18.02 | 13.96 | 12.73 | 68.51 | 43.78 | 42.62 | 151.79 | 388.33 | 53.65 | 52.36 | 25.53 | 77.07 | 81.69 | 71.23 | 0 | 0 | 10.68 | 10.26 | 10.22 | 10.31 | -1 | -1 | -1 | -1 | 381.15 | 772 | 17:21:45 | 10.5167 | 772 | 0 | 0 | 0 | 18.4467 | 25.44 | 6.9933 | 10.1726 | 10.6346 | 10.2021 | 79.38 | 10.5192 | -0.43254 | -0.22864 | 0.1154 | -0.088493 | 615 | 0.29025 | 0.34249 | 395 | 0.18642 | 0.21997 | 89.3251 | -68.4963 | 304.5986 | -233.5723 | 2409.5335 | 8216.5093 | -215.0332 | -113.6683 | -733.2633 | -387.6088 | 7483.246 | 7982.9369 | 9.6933 | 10.3406 | 786.2 | 7618.6322 | 9.6904 | -531.2991
| 17:21:55 | 25.21 | 37.36 | 24.53 | 19.26 | 18.54 | 18.23 | 17.72 | 17.33 | 19.34 | 19.55 | 17.85 | 13.95 | 12.7 | 68.58 | 43.77 | 42.69 | 152.22 | 388.57 | 54.07 | 52.57 | 25.77 | 77.25 | 81.79 | 71.22 | 0 | 0 | 10.58 | 10.35 | 10.45 | 10.29 | -1 | -1 | -1 | -1 | 381.15 | 773 | 17:21:55 | 10.6833 | 773 | 0 | 0 | 0 | 18.4033 | 25.21 | 6.8067 | 10.3981 | 10.5305 | 10.2996 | 79.52 | 10.509 | -0.23092 | -0.13115 | 0.021488 | -0.078281 | 615 | 0.29025 | 0.34249 | 395 | 0.18642 | 0.21997 | 16.6326 | -60.5922 | 56.7171 | -206.6195 | 2345.218 | 7997.1935 | -114.7989 | -65.1992 | -391.4643 | -222.3294 | 7605.7292 | 7790.574 | 9.8392 | 10.0784 | 783 | 7628.2908 | 9.7425 | -486.3933
| 17:22:06 | 25.27 | 37.42 | 24.61 | 19.26 | 18.58 | 18.29 | 17.82 | 17.39 | 19.34 | 19.63 | 17.81 | 14.03 | 12.71 | 68.64 | 43.81 | 42.7 | 152.1 | 388.86 | 54.07 | 52.57 | 25.77 | 77.25 | 81.79 | 71.22 | 0 | 0 | 10.62 | 10.39 | 10.5 | 10.32 | -1 | -1 | -1 | -1 | 381.15 | 792 | 17:22:06 | 10.8667 | 792 | 0 | 0 | 0 | 18.4467 | 25.27 | 6.8233 | 10.4488 | 10.5688 | 10.3338 | 79.52 | 10.5381 | -0.23503 | -0.096951 | 0.030715 | -0.10736 | 615 | 0.29025 | 0.34249 | 395 | 0.18642 | 0.21997 | 23.7742 | -83.0998 | 81.0699 | -283.3703 | 2350.9605 | 8016.7753 | -116.8412 | -48.1986 | -398.4285 | -164.3571 | 7618.3468 | 7733.4049 | 9.6191 | 9.7644 | 783.2 | 7602.7846 | 9.7079 | -527.9565
| 17:22:17 | 25.33 | 37.4 | 24.46 | 19.18 | 18.59 | 18.24 | 17.69 | 17.32 | 19.35 | 19.62 | 17.77 | 14.06 | 12.71 | 68.71 | 43.78 | 42.68 | 152.06 | 389.25 | 54.3 | 52.99 | 25.77 | 77.25 | 81.69 | 71.44 | 0 | 0 | 10.74 | 10.37 | 10.45 | 10.3 | -1 | -1 | -1 | -1 | 381.15 | 793 | 17:22:17 | 11.05 | 793 | 0 | 0 | 0 | 18.395 | 25.33 | 6.935 | 10.3987 | 10.6935 | 10.3224 | 79.47 | 10.4967 | -0.37107 | -0.10836 | 0.19672 | -0.065982 | 615 | 0.29025 | 0.34249 | 395 | 0.18642 | 0.21997 | 152.2703 | -51.072 | 519.2419 | -174.1556 | 2389.4349 | 8147.9731 | -184.473 | -53.871 | -629.0529 | -183.7 | 7518.9202 | 7973.8175 | 9.4816 | 10.0553 | 783.8 | 7559.6503 | 9.6461 | -573.4406
| 17:22:27 | 25.18 | 37.51 | 24.54 | 19.2 | 18.6 | 18.31 | 17.71 | 17.3 | 19.28 | 19.62 | 17.89 | 14.05 | 12.7 | 68.8 | 43.91 | 42.84 | 152.44 | 389.53 | 54.3 | 52.78 | 25.78 | 77.27 | 81.69 | 71.34 | 0 | 0 | 10.6 | 10.44 | 10.5 | 10.3 | -1 | -1 | -1 | -1 | 381.16 | 794 | 17:22:27 | 11.2167 | 794 | 0 | 0 | 0 | 18.4 | 25.18 | 6.78 | 10.4494 | 10.5541 | 10.3894 | 79.48 | 10.5014 | -0.16474 | -0.041371 | 0.052693 | -0.070673 | 615 | 0.29025 | 0.34249 | 395 | 0.18642 | 0.21997 | 40.7858 | -54.7033 | 139.0796 | -186.5382 | 2336.0301 | 7965.8627 | -81.8975 | -20.5671 | -279.2704 | -70.1337 | 7686.5923 | 7779.3245 | 9.6808 | 9.7976 | 784.8 | 7582.5669 | 9.6628 | -486.2959
| 17:22:38 | 25.48 | 37.47 | 24.47 | 19.32 | 18.6 | 18.3 | 17.71 | 17.37 | 19.39 | 19.64 | 17.82 | 14.12 | 12.75 | 68.85 | 43.9 | 42.79 | 152.75 | 390.09 | 53.88 | 52.68 | 25.56 | 77.17 | 81.69 | 71.24 | 0 | 0 | 10.77 | 10.33 | 10.37 | 10.32 | -1 | -1 | -1 | -1 | 381.16 | 794 | 17:22:38 | 11.4 | 794 | 0 | 0 | 0 | 18.4483 | 25.48 | 7.0317 | 10.3232 | 10.7266 | 10.2765 | 79.43 | 10.5271 | -0.45012 | -0.15422 | 0.19955 | -0.096349 | 615 | 0.29025 | 0.34249 | 395 | 0.18642 | 0.21997 | 154.462 | -74.5775 | 526.7154 | -254.3093 | 2422.7412 | 8261.5473 | -223.7738 | -76.6672 | -763.0687 | -261.435 | 7498.4786 | 8007.2381 | 9.4439 | 10.0847 | 789.2 | 7585.6134 | 9.6129 | -492.257
| 17:22:48 | 25.3 | 37.59 | 24.43 | 19.25 | 18.57 | 18.31 | 17.78 | 17.41 | 19.34 | 19.58 | 17.7 | 14.04 | 12.74 | 68.87 | 43.98 | 42.87 | 152.56 | 390.73 | 53.88 | 52.77 | 25.56 | 77.06 | 81.79 | 71.04 | 0 | 0 | 10.68 | 10.39 | 10.34 | 10.3 | -1 | -1 | -1 | -1 | 381.16 | 794 | 17:22:48 | 11.5667 | 794 | 0 | 0 | 0 | 18.4433 | 25.3 | 6.8567 | 10.2981 | 10.629 | 10.3448 | 79.425 | 10.5231 | -0.28418 | -0.085933 | 0.10592 | -0.09232 | 615 | 0.29025 | 0.34249 | 395 | 0.18642 | 0.21997 | 81.9877 | -71.459 | 279.578 | -243.6752 | 2362.4454 | 8055.9388 | -141.2761 | -42.7209 | -481.7516 | -145.6784 | 7574.1872 | 7812.2636 | 9.5393 | 9.8391 | 793.4 | 7579.305 | 9.553 | -510.3144
| 17:22:58 | 25.45 | 37.51 | 24.45 | 19.27 | 18.65 | 18.35 | 17.83 | 17.4 | 19.37 | 19.61 | 17.58 | 14.11 | 12.8 | 68.94 | 43.95 | 42.88 | 151.77 | 390.45 | 54.1 | 52.78 | 25.56 | 77.27 | 82.01 | 71.34 | 0 | 0 | 10.78 | 10.35 | 10.4 | 10.35 | -1 | -1 | -1 | -1 | 381.16 | 793 | 17:22:58 | 11.7333 | 793 | 0 | 0 | 0 | 18.4783 | 25.45 | 6.9717 | 10.3535 | 10.7279 | 10.2992 | 79.64 | 10.5756 | -0.42865 | -0.1315 | 0.15229 | -0.14486 | 615 | 0.29025 | 0.34249 | 395 | 0.18642 | 0.21997 | 117.8786 | -112.1266 | 401.9661 | -382.3516 | 2402.0683 | 8191.053 | -213.1007 | -65.3738 | -726.6735 | -222.9247 | 7464.3795 | 7808.7014 | 9.4128 | 9.847 | 793.6 | 7548.5116 | 9.5117 | -575.9634
| 17:23:09 | 25.46 | 37.57 | 24.48 | 19.36 | 18.54 | 18.3 | 17.81 | 17.47 | 19.46 | 19.62 | 17.78 | 14.02 | 12.72 | 68.96 | 43.94 | 42.8 | 152.61 | 389.88 | 54.09 | 52.99 | 25.56 | 77.27 | 81.81 | 71.44 | 0 | 0 | 10.82 | 10.38 | 10.42 | 10.36 | -1 | -1 | -1 | -1 | 381.17 | 793 | 17:23:09 | 11.9167 | 793 | 0 | 0 | 0 | 18.49 | 25.46 | 6.97 | 10.3704 | 10.7778 | 10.3334 | 79.54 | 10.57 | -0.44443 | -0.097341 | 0.20787 | -0.13921 | 615 | 0.29025 | 0.34249 | 395 | 0.18642 | 0.21997 | 160.9013 | -107.7552 | 548.6736 | -367.4454 | 2401.4941 | 8189.0948 | -220.9442 | -48.3924 | -753.4198 | -165.0182 | 7435.675 | 7821.6494 | 9.3766 | 9.8634 | 793.6 | 7531.8625 | 9.4907 | -600.8368
| 17:23:19 | 25.26 | 37.61 | 24.4 | 19.24 | 18.6 | 18.34 | 17.79 | 17.4 | 19.4 | 19.64 | 17.86 | 14.05 | 12.75 | 69.02 | 43.98 | 42.89 | 151.85 | 390.73 | 53.88 | 52.89 | 25.56 | 77.27 | 81.7 | 71.25 | 0 | 0 | 10.68 | 10.41 | 10.33 | 10.33 | -1 | -1 | -1 | -1 | 381.17 | 794 | 17:23:19 | 12.0833 | 794 | 0 | 0 | 0 | 18.4617 | 25.26 | 6.7983 | 10.2793 | 10.6278 | 10.3562 | 79.485 | 10.5435 | -0.27159 | -0.074514 | 0.084354 | -0.11272 | 615 | 0.29025 | 0.34249 | 395 | 0.18642 | 0.21997 | 65.2931 | -87.2493 | 222.6495 | -297.5203 | 2342.3468 | 7987.4026 | -135.0183 | -37.0439 | -460.4125 | -126.3197 | 7526.9901 | 7689.8823 | 9.4798 | 9.685 | 793.6 | 7499.9421 | 9.4505 | -637.0652
| 17:23:30 | 25.48 | 37.65 | 24.56 | 19.31 | 18.7 | 18.4 | 17.86 | 17.44 | 19.45 | 19.65 | 17.73 | 14.08 | 12.79 | 69.05 | 44.04 | 42.92 | 152.15 | 390.81 | 53.9 | 52.47 | 25.57 | 77.28 | 81.82 | 71.25 | 0 | 0 | 10.73 | 10.44 | 10.43 | 10.37 | -1 | -1 | -1 | -1 | 381.17 | 776 | 17:23:30 | 12.2667 | 776 | 0 | 0 | 0 | 18.5267 | 25.48 | 6.9533 | 10.3838 | 10.6832 | 10.3832 | 79.55 | 10.596 | -0.29992 | -0.047513 | 0.087114 | -0.1653 | 615 | 0.29025 | 0.34249 | 395 | 0.18642 | 0.21997 | 67.4289 | -127.9444 | 229.9327 | -436.2904 | 2395.7516 | 8169.513 | -149.1045 | -23.6208 | -508.4463 | -80.5469 | 7661.0667 | 7733.2226 | 9.8725 | 9.9655 | 790 | 7532.4597 | 9.5362 | -586.1408
end test | 17:23:40 | 25.41 | 37.59 | 24.52 | 19.36 | 18.58 | 18.35 | 17.79 | 17.42 | 19.46 | 19.67 | 17.83 | 14.05 | 12.74 | 69.16 | 44 | 42.93 | 152.38 | 390.62 | 53.69 | 52.57 | 25.46 | 77.07 | 81.7 | 71.25 | 0 | 0 | 10.71 | 10.35 | 10.36 | 10.34 | -1 | -1 | -1 | -1 | 381.17 | 776 | 17:23:40 | 12.4333 | 776 | 0 | 0 | 0 | 18.4933 | 25.41 | 6.9167 | 10.3175 | 10.6587 | 10.3037 | 79.385 | 10.5513 | -0.35501 | -0.12708 | 0.10743 | -0.12051 | 615 | 0.29025 | 0.34249 | 395 | 0.18642 | 0.21997 | 83.153 | -93.2764 | 283.5516 | -318.0725 | 2383.1182 | 8126.4332 | -176.4914 | -63.175 | -601.8356 | -215.4267 | 7524.5975 | 7808.3606 | 9.6966 | 10.0623 | 786.4 | 7522.5418 | 9.5677 | -610.1576
-43.2
-43.0167
-42.85
-42.6833
-42.5167
-42.3333
-42.1667
-41.9833
-41.8
-41.6167
-41.45
-41.2833
-41.1167
-40.9333
-40.7667
-40.6
-40.4333
-40.25
-40.05
-39.85
-39.6833
-39.5
-39.3333
-39.15
-38.9667
-38.8
-38.6333
-38.45
-38.2667
-38.1
-37.9167
-37.7333
-37.5667
-37.3833
-37.2
-37.0333
-36.8667
-36.7
-36.5167
-36.3
-36.1333
-35.95
-35.7833
-35.6167
-35.4333
-35.25
-35.0833
-34.9167
-34.75
-34.5667
-34.4
-34.2333
-34.05
-33.8833
-33.7
-33.5333
-33.3667
-33.1833
-33.0167
-32.8333
-32.65
-32.4667
-32.3
-32.1333
-31.95
-31.7833
-31.6
-31.4333
-31.2667
-31.1
-30.9167
-30.7333
-30.5667
-30.4
-30.2333
-30.0667
-29.8833
-29.7
-29.5333
-29.3667
-29.1833
-29.0167
-28.8333
-28.6667
-28.4833
-28.3167
-28.1333
-27.9667
-27.7833
-27.5833
-27.4
-27.2167
-27.05
-26.8667
-26.6833
-26.4833
-26.3167
-26.1333
-25.95
-25.7833
-25.6167
-25.4333
-25.25
-25.0667
-24.9
-24.7167
-24.55
-24.3667
-24.1833
-24.0167
-23.8
-23.6167
-23.45
-23.2667
-23.0833
-22.9167
-22.75
-22.5667
-22.4
-22.2167
-22.0333
-21.8333
-21.6333
-21.4333
-21.2667
-21.1
-20.9167
-20.7333
-20.5333
-20.35
-20.1833
-20.0167
-19.8333
-19.6667
-19.4833
-19.3167
-19.1333
-18.95
-18.7833
-18.6167
-18.4333
-18.2667
-18.0833
-17.9167
-17.75
-17.5667
-17.4
-17.2333
-17.0667
-16.8833
-16.7
-16.5333
-16.35
-16.1667
-16
-15.8167
-15.6333
-15.4333
-15.25
-15.0667
-14.8833
-14.7
-14.5167
-14.35
-14.1833
-14
-13.8333
-13.6667
-13.4833
-13.3167
-13.1333
-12.9667
-12.8
-12.6333
-12.4333
-12.2667
-12.1
-11.9167
-11.75
-11.55
-11.3833
-11.2
-11.0333
-10.8667
-10.6833
-10.5167
-10.3333
-10.1667
-10
-9.8167
-9.6167
-9.4333
-9.2667
-9.1
-8.9167
-8.75
-8.5833
-8.4
-8.2
-8.0333
-7.8333
-7.6667
-7.4833
-7.3167
-7.1333
-6.9667
-6.8
-6.6167
-6.4333
-6.2667
-6.1
-5.9333
-5.75
-5.5833
-5.4167
-5.25
-5.0833
-4.9
-4.7333
-4.5667
-4.3833
-4.2167
-4.0333
-3.8667
-3.7
-3.5167
-3.3
-3.1333
-2.95
-2.7833
-2.6
-2.4167
-2.25
-2.0833
-1.9167
-1.7333
-1.55
-1.3833
-1.2167
-1.05
-0.86667
-0.7
-0.51667
-0.33333
-0.16667